| Client: |  |  |  |  |  |  | Contract No: |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Project: |  |  |  |  |  |  | Document No: |  |  |  |  |  |  |  | Revision: |  |  |  |  |
| Area/System No: |  |  |  |  |  |  | Area/System Description: |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Document |  |  |  |  |  | Controlling Document |  |  |  |  |  |  |  | Verifying Documents |  |  |  |  |  |
| No. | Title |  |  |  |  | No. |  | Title |  |  |  |  |  | No. |  |  | Title |  |  |
|  | BGER Project Quality Management Plan (PQMP) |  |  |  |  | AS/NZS 3000 |  | Wiring rules |  |  |  |  |  |  |  |  | Material certificates |  |  |
|  | Mobilisation, education and training procedure |  |  |  |  |  |  | Client’s specifications |  |  |  |  |  |  |  |  | Tools calibration certificates |  |  |
|  | Punch list procedure |  |  |  |  |  |  | AFC Dawings |  |  |  |  |  |  |  |  | Client’s ITRs |  |  |
|  | “As-built” procedure |  |  |  |  |  |  | 3D model |  |  |  |  |  |  |  |  | Delivery Packing List |  |  |
|  |  |  |  |  |  | AS/NZS 1554.1 |  | Structural steel welding |  |  |  |  |  |  |  |  | Training register |  |  |
|  |  |  |  |  |  | AS/NZS 4100 |  | Steel Structures |  |  |  |  |  |  |  |  | As-built register |  |  |
|  |  |  |  |  |  | AS/NZS 3012 |  | Electrical installations - Construction and demolition sites |  |  |  |  |  |  |  |  | Approved WPS and WQR |  |  |
|  |  |  |  |  |  | AS/NZS 3760 |  | In-service safety inspection and testing of electrical equipment and RCDs |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | AS/NZS 2053 |  | Conduits and fittings for electrical installations Flexible conduits and fittings of metal or composite material |  |  |  |  |  |  |  |  |  |  |  |
| Legend |  |  |  |  |  |  |  |  |  |  | Approval and Change History |  |  |  |  |  |  |  |  |
| Verification Activity |  |  |  |  |  |  |  |  |  |  | Rev | Details |  | Date |  | Prepared by (BGER) |  |  | Client Approval (XXX) |
| H – Hold Point |  |  | Work shall not proceed past the Hold Point until released by the Organisation imposing the Hold Point. 48 hrs. notice required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| W – Witness Point |  |  | An Inspection Point that may be witnessed by the Organisation imposing the Witness Point. 48 hrs. notice required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I – Inspection |  |  | Formal inspection activity to be undertaken and recorded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| S – Surveillance |  |  | An activity that is subject to on-going monitoring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| R – Review |  |  | Review of text reports/records or other evidence of compliance. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Responsible Person (RP) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUP |  |  | Supervisor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QR |  |  | Quality Representative (Project Engineer) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUR |  |  | Surveyor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Item | Activity/Operations/Stage No. | Controlling Document/ Procedure | Standard, Spec, Drawing Ref or Acceptance Criteria | Verifying Document/ Report/ Certificate | Verification Activity by |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | BGER RP | BGER/ sign | Client/ sign |  |
| 1.0 | Approvals |  |  |  |  |  |  |  |
| 1.1 | Prepare BGER’s ITP and submit to Client for Approval | PQMP | ITP | Approved ITP | QR | H | H |  |
| 1.2 | Confirm correct competent person, training, qualification and VOC’s are correct | PQMP | Mobilisation, education and training procedure | Training register | SUP | H | H |  |
| 1.3 | Submit and obtain approval for Weld Procedure Specifications and Welder Qualifications | PQMP | AS/NZS 1554.1 | Approved WPS and WQR | QR | H | H |  |
| 2.0 | Material Receipt |  |  |  |  |  |  |  |
| 2.1 | Check material for damage due to delivery and fabrication defect | PQMP | AFC Drawing | Delivery Packing List, Material Inspection Report | QR | I, R | R |  |
| 2.2 | Confirm correct material received | PQMP | Client’s specs | Material Certificates | QR | I, R | R |  |
| 2.3 | Check that correct quantities and dimensions of material and consumables are delivered | PQMP | AFC Drawing, Bill of Material | Material Inspection Report, Electrical consumables material certificates | QR | I, R | R |  |
| 2.4 | Ensure all test equipment is calibrated and registered. Ensure all construction equipment and tooling are tested and correct tag is in place. | PQMP | Control of test equipment procedure AS/NZS 3012 AS/NZS 3760 | Calibration and records register | SUP | I, R | S |  |
| 3.0 | Scope Of Work |  |  |  |  |  |  |  |
| 3.1 | Confirm the location and positioning of cable way are installed correctly | PQMP | AFC Layout Drawings 3D model | Client’s ITR | QR | I, H | R |  |
| 3.2 | Check the cable ladder/tray brackets & supports are correctly installed and bolts/clamps are snug tight. | PQMP | AFC Drawings AS 4100 Steel Structures | Client’s ITR | SUP | I | R |  |
| 3.3 | Confirm walkway and head clearance is acceptable | PQMP | AFC Layout Drawings Client’s specs | Client’s ITR | SUP | I | R |  |
| 3.4 | Check cable ladder/tray for sharp edges and cuts ends, all welded and cut ends to be touch up painted as per specs | PQMP | Client’s specs -protective coatings | Client’s ITR | QR | H | H |  |
| 3.5 | Check the cable ladder earthing and conduct continuity test as required | PQMP | AS/NZS 3000 Wiring Rules | Client’s ITR | SUP | I | R |  |
| 3.6 | Confirm barrier strips are installed as required | PQMP | Client’s specs | Client’s ITR | SUP | I | R |  |
| 3.7 | Confirm correct sun cover is installed with correct anchoring arrangement | PQMP | Client’s specs | Client’s ITR | SUP | I | R | Should after cable testing is completed |
| 3.8 | Confirm conduits are fastened to structures at correct distances | PQMP | Client’s specs AS/NZS 2053 | Client’s ITR | SUP | I | R |  |
| 4.0 | Inspection verification and finishing works |  |  |  |  |  |  |  |
| 4.1 | Walk down, Inspection and Works to go list generated, rectified and closed out | PQMP | Punch list procedure | Works to go list | QR/SUP | I | S |  |
| 5.0 | Quality Documents |  |  |  |  |  |  |  |
| 5.1 | Verify all drawings related are complete and submitted “As-built” status | PQMP | Client “As-built” procedure | As-built register | QR | H | H |  |
| 5.1 | Completion of MDR | PQMP | Client’ Specs | MDR progressive review and sign off | QR | R | R |  |