## Register
INSPECTION AND TEST PLAN (ITP) REGISTER
|  | CLIENT : | Fortescue Metals Group
|  | PROJECT : | Solomon Bulk Ammonium Nutrate Storage Facility
|  | PROJECT No : | 2704
|  | SITE : | Solomon
|  | LAST UPDATED : | 2014-10-09
ITR No. | Title |  |  | Originator | Date Issued | Date Completed
ITP-001 | EARTHWORKS |  |  | Darren Duthie | XX/XX/XXXX | XX/XX/XXXX
ITP-002 | CIVIL WORKS |  |  | Darren Duthie | XX/XX/XXXX | XX/XX/XXXX
ITP-003 |  |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX

## ITP-001
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  | INSPECTION AND VERIFICATION
[9 empty] | Primero |  | Client |  | 3rd Party Inspection
[9 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Preceding Tasks
1.1 | Site Handover |  |  | Handover Letter |  | Sign and Approve Handover Letter | TO BE CONSTRUCTED |  | H |  | H
1.2 | Specification Sign Off |  |  | 100-SP-CI-0007 100-SP-CI-0004 100-SP-CI-0002 |  | Approval of Specification Documents | TO BE CONSTRUCTED |  | H |  | H
1.3 | Bulk Compaction Testing Sign Off |  |  | Bulk Compaction Test Results |  | Approval of Bulk Compaction Test Results | TO BE CONSTRUCTED |  | H |  | H
4 | Material Compliance and Certification
4.1 | Crushed Rock |  |  | 100-SP-CI-0007 |  | Comply with Specifications and Standards |  |  | W |  | M
4.2 | Fill Materials |  |  | 100-SP-CI-0007 AS 1289 AS 1152 AS 1141 |  | Comply with Specifications and Standards |  |  | W |  | M
5 | Excavation
5.1 | Approved Drawings |  |  | AFC Drawings |  | Approval of Drawings | 02704-ITR-001 |  | H |  | M
5.2 | Approved Specification |  |  | 100-SP-CI-0007 |  | Approval of Specification | 02704-ITR-001 |  | H |  | H
6 | Backfill
6.1 | Compaction Thickness Layers |  |  | 100-SP-CI-0007 |  | Comply with Specifications | 02704-ITR-001 |  | W |  | M
7 | Compaction
7.1 | Compaction Thickness Layers |  |  | 100-SP-CI-0007 |  | Comply with Specifications | 02704-ITR-001 |  | W |  | M
8 | Tolerance of Earthworks
8.1 | Surface Levels |  |  | 100-SP-CI-0007 Section 15 |  |  | 02704-ITR-001 |  | W |  | M
8.2 | Grade Condition |  |  | 100-SP-CI-0007 Section 15 |  |  | 02704-ITR-001 |  | W |  | M
8.3 | Finishing Tolerances |  |  | 100-SP-CI-0007 Section 15 |  |  | 02704-ITR-001 |  | W |  | H
9 | Earthworks Testing
9.1 | Instrument Calibration |  |  | 100-SP-CI-0007 Section 16.3 |  |  | Calibration Certificate |  | W |  | W
9.2 | Acceptance Testing |  |  | 100-SP-CI-0007 Section 13.3 100-SP-CI-0007 Section 16.4 |  |  | Compaction Certificate |  | W |  | M
9.3 | Frequency of Testing |  |  | 100-SP-CI-0007 Section 13.4 100-SP-CI-0007 Appendix 1 & 2 AS3798-2007 Table 8.1 |  |  | NATA Certificate |  | W |  | M
|  |  | PRIMERO |  |  |  | FORTESCUE METALS GROUP LTD.
Name: (print)
Position Title
Signature
Date
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  | R & C = REVIEW & COMMENT

## ITP-002
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. | ACCEPTANCE CRITERIA |  | VERIFYING DOCUMENT | INSPECTION AND VERIFICATION
[8 empty] | Primero |  | Client |  | 3rd Party Inspection
[8 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Planning
1.1 | Quality Management Plan |  |  |  | Submitted & Approved |  |  | H |  | H
1.2 | Construction Drawings |  |  |  | AFC Drawings |  |  | H |  | H
1.3 | Safe Work Instructions |  |  |  | Submitted & Approved |  |  | R |  | R
1.4 | Approval of Concrete Mix Design |  |  | AFC Drawings | AS-1379 |  | NATA Test Results | R |  | H
Trial Mix
2 | Formwork Installation
2.1 | Confirm formwork is secured to |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 |  |  | M
| correct lines and levels |  |  |  | Formwork Drawings |  |  | W
AS-3610
2.2 | Survey formwork to ensure within |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
| tolerance |  |  |  | AS-3610
2.3 | Inspect formwork to ensure |  |  | 100-SP-CI-0003 | Formwork Drawings |  | ITR 203, ITR-204 | W |  | M
| compliance to design |  |  |  | AFC Drawings
3 | Reinforcment Installation
3.1 | Reinforcement is processed, bent to |  |  | 100-SP-CI-0003 | AS-4671 |  | ISO 9001 | R |  | R
| specifications | [5 empty] | ACRS Certificates
Mill Certificates
3.2 | Reinforcement is bundled, tagged and stored to |  |  | 100-SP-CI-0003 | AS-4671 |  | Delivery Schedules | W,R |  | M
specifications
3.1 | Ensure all materials are clean, cut and bent to |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | M |  | M
| schedules |  |  |  | AS-4671
3.2 | Confirm all reinforcement is in place and secured |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
3.3 | Check cover is in compliance to specifications |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
and drawings
3.4 | Ensure all supports, chairs, blocks are in place |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
3.5 | Verify splicing is as per drawings and |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
| specifications |  |  |  | AS-3600
3.6 | Check reinforcement is sufficiently fixed |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
4 | Embedments
4.1 | Embedments are to specifications, |  |  | 100-SP-CI-0003 | AFC Drawings |  | Vendor's ITP | W |  | W
| HD bolts, cast in angles, plates and | [5 empty] | Mill Certificates
| ferrules | [5 empty] | WPQ's, WP's
[5 empty] | AS-4100 |  | Galvanising reports
Material reports
ITR 203, ITR-204
4.2 | Lifting anchors and brace points |  |  | Approved engineered | AS-3850 |  | Manufacturer's report | W |  | W
|  |  |  | shop drawings | AS-3600 |  | Lifting engineered design
ITR-204
4.3 | Placement of embedment items are to |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
specifications and drawings
4.4 | Final visual inspection of all embedments |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | W |  | M
4.5 | Final pre pour survey of embedment items |  |  | 100-SP-CI-0003 | Survey Report |  | ITR 203, ITR-204 | W |  | R
placement to ensure within tolerance
5 | Concrete Placement
5.1 | Signed off Concrete Pre Pour ITR's |  |  | 100-SP-CI-0003 | AFC Drawings |  | ITR 203, ITR-204 | H |  | H
5.2 | Correct Mix Code Delivered |  |  | 100-SP-CI-0003 | AFC Drawings |  | Batch Docket | W |  | M
Trial Mix
5.3 | Concrete Testing - Temperture, Slump Strength |  |  | 100-SP-CI-0003 | AS-1012 |  | Field Testing Sheet | W |  | R
[5 empty] | AS-1379 |  | NATA Test Results
5.4 | Concrete placement |  |  | 100-SP-CI-0003 | AS-3600 |  | ITR 203, ITR-204 | W |  | M
AFC Drawings
5.5 | Construction Joints |  |  | 100-SP-CI-0003 | AS-3600 |  | ITR-206 | W |  | M
AFC Drawings
5.6 | Compaction |  |  | 100-SP-CI-0003 |  |  | ITR 203, ITR-204 | W |  | M
5.7 | Curing |  |  | 100-SP-CI-0003 | AS-3799 |  | ITR 203, ITR-204 | W |  | M
Manufacturer's TDS
5.8 | Inspect concrete surfaces after formwork removal |  |  | 100-SP-CI-0003 | AS3600 |  | ITR-206 | W |  | R
5.9 | Concrete Repairs |  |  | 100-SP-CI-0003 | Approved Concrete |  | ITR-206 | W |  | W
Repair Methodology
6 | Inspection
6.1 | Survey and issue as built of completed structure |  |  | 100-SP-CI-0003 | AFC Drawings |  | Survey Reports | H |  | R
7 | Close Out Documentation
7.1 | Compile and submit all signed QA documentation |  |  | 100-SP-CI-0003 |  |  | MDR | R,S |  | R
|  |  | PRIMERO |  |  |  | FORTESCUE METALS GROUP LTD.
Name: (print)
Position Title
Signature
Date
LEGEND |  | H = HOLD POINT |  | ACT = ACTIVITY |  | R/A = REVIEW & APPROVE DOC. |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  | W = WITNESS POINT |  | V = VISUAL INSPECTION |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  | W @ R = WITNESS @ RANDOM |  | A = APPROVE |  | R & C = REVIEW & COMMENT

## ITP-002 (2)
REF | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR PROCEDURE ETC. | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3rd Party Inspection
[5 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | PLANNING
1.1 | Quality Management Plan |  | Submitted & Approved |  | H |  | H
1.2 | Construction Drawings |  | AFC Drawings |  | H |  | H
1.3 | Safe Work Instructions |  | Submitted & Approved |  | R |  | R
1.4 | Approval of Concrete Mix Design | AFC Drawings | AS-1379; Trial Mix | NATA Test Results | R |  | H
2 | FORMWORK INSTALLATION
2.1 | Confirm formwork is secured to correct lines and levels | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
|  |  | Formwork Drawings | ITR 203, ITR-204 | W |  | M
|  |  | AS-3610 | ITR 203, ITR-204 | W |  | M
2.2 | Survey formwork to ensure within tolerance | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
|  |  | AS-3610 | ITR 203, ITR-204 | W |  | M
2.3 | Inspect formwork to ensure compliance to design | 100-SP-CI-0003 | Formwork Drawings | ITR 203, ITR-204 | W |  | M
|  |  | AFC Drawings | ITR 203, ITR-204 | W |  | M
3 | REINFORCMENT INSTALLATION
3.1 | Reinforcement is processed, bent to specifications | 100-SP-CI-0003 | AS-4671 | ISO 9001 | R |  | R
|  |  |  | ACRS Certificates | R |  | R
|  |  |  | Mill Certificates | R |  | R
3.2 | Reinforcement is bundled, tagged and stored to specifications | 100-SP-CI-0003 | AS-4671 | Delivery Schedules | W,R |  | M
3.1 | Ensure all materials are clean, cut and bent to schedules | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | M |  | M
|  |  | AS-4671 | ITR 203, ITR-204 | M |  | M
3.2 | Confirm all reinforcement is in place and secured | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
3.3 | Check cover is in compliance to specifications and drawings | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
3.4 | Ensure all supports, chairs, blocks are in place | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
3.5 | Verify splicing is as per drawings and specifications | 100-SP-CI-0003 | AFC Drawings; AS-3600 | ITR 203, ITR-204 | W |  | M
3.6 | Check reinforcement is sufficiently fixed | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
4 | EMBEDMENTS
4.1 | Embedments are to specifications, HD bolts, cast in angles, plates and ferrules | 100-SP-CI-0003 | AFC Drawings | Vendor's ITP | W |  | W
|  |  |  | Mill Certificates | W |  | W
|  |  |  | WPQ's, WP's | W |  | W
|  |  | AS-4100 | Galvanising reports | W |  | W
|  |  |  | Material reports | W |  | W
|  |  |  | ITR 203, ITR-204 | W |  | W
4.2 | Lifting anchors and brace points | Approved engineered shop drawings | AS-3850 | Manufacturer's report | W |  | W
|  |  | AS-3600 | Lifting engineered design | W |  | W
|  |  |  | ITR-204 | W |  | W
4.3 | Placement of embedment items are to specifications and drawings | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
4.4 | Final visual inspection of all embedments | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
4.5 | Final pre pour survey of embedment items placement to ensure within tolerance | 100-SP-CI-0003 | Survey Report | ITR 203, ITR-204 | W |  | R
5 | CONCRETE PLACEMENT
5.1 | Signed off Concrete Pre Pour ITR's | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | H |  | H
5.2 | Correct Mix Code Delivered | 100-SP-CI-0003 | AFC Drawings | Batch Docket | W |  | M
|  | Trial Mix | AFC Drawings | Batch Docket | W |  | M
5.3 | Concrete Testing - Temperture, Slump Strength | 100-SP-CI-0003 | AS-1012 | Field Testing Sheet | W |  | R
|  |  | AS-1379 | NATA Test Results
5.4 | Concrete placement | 100-SP-CI-0003 | AS-3600 | ITR 203, ITR-204 | W |  | M
|  |  | AFC Drawings | ITR 203, ITR-204
5.5 | Construction Joints | 100-SP-CI-0003 | AS-3600 | ITR-206 | W |  | M
|  |  | AFC Drawings | ITR-206 | W |  | M
5.6 | Compaction | 100-SP-CI-0003 |  | ITR 203, ITR-204 | W |  | M
5.7 | Curing | 100-SP-CI-0003 | AS-3799 | ITR 203, ITR-204 | W |  | M
|  |  |  | Manufacturer's TDS | W |  | M
5.8 | Inspect concrete surfaces after formwork removal | 100-SP-CI-0003 | AS3600 | ITR-206 | W |  | R
|  |  |  | ITR-206 | W |  | R
5.9 | Concrete Repairs | 100-SP-CI-0003 | Approved Concrete | ITR-206 | W |  | W
|  |  | Repair Methodology | ITR-206 | W |  | W
6 | INSPECTION
6.1 | Survey and issue as built of completed structure | 100-SP-CI-0003 | AFC Drawings | Survey Reports | H |  | R
7 | CLOSE OUT DOCUMENTATION
7.1 | Compile and submit all signed QA documentation | 100-SP-CI-0003 |  | MDR | R,S |  | R
8 | APPROVALS
|  | PRIMERO GROUP PTY LTD |  | FORTESCUE METALS GROUP LTD.
Name: (print)
Position Title
Signature
Date
LEGEND | H = HOLD POINT | ACT = ACTIVITY | R/A = REVIEW & APPROVE DOC. |  | D = DIMENSIONAL INSPECTION
| S = SUBMIT DOCUMENT TO CLIENT | W = WITNESS POINT | V = VISUAL INSPECTION |  | V/S = VERIFYING SIGNATURE
| M = MONITOR ON A RANDOM BASIS | W @ R = WITNESS @ RANDOM | A = APPROVE |  | R & C = REVIEW & COMMENT

## ITP-003
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 1 of 4
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | - Structural | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger |  |  |  | - Mechanical
|  | Final Release/Responsibility by: | [6 empty] | - Piping | Primero Doc No.: |  |  | 02704-ITP-CI-003
|  | CLIENT APPROVAL | [6 empty] | Fabrication | Client Doc No.:
(OFFSITE)
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Design/Specifications
1.1 | Review Scope of Work and relevant specifications |  |  | Client SOW 100-SP-ME-0002 100-SP-ME-0003 100-SP-ME-0004 100-SP-ME-0042 100-SP-PI-0001 100-SP-ST-0001 100-SP-ST-0002 100-SP-ST-0003 100-SP-ST-0004
1.2 | Review Drawings and Data Sheets |  |  | AFC Drawings Data Sheets
2 | Approvals
2.1 | Submit Project Documentation, ITP, NDE Procedures, Pressure Testing Procedure |  |  | ITP NDE Procedures Pressure Testing Procedures
2.2 | Submit Weld Procedure Specifications & Qualifications |  |  | WPS & WPQ Reports
2.3 | Submit Welder Qualifications |  |  | Welder Qualification Reports and Register
3 | Materials
3.1 | Monitor Incoming Materials (New) and Client Supply |  |  | Clinet MTO AFC Drawings
3.2 | Material Traceability |  |  | AFC Drawings Material Control Procedure Client Specifications
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 2 of 4
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Concrete | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Darren Duthie
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-003
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
4 | Materials Preparation
4.1 | Mark materials for cutting & weld preparation. Dimensional check.
4.2 | Prepare controlled/cut materials for fabrication
4.3 | Consumables Control
5 | Fabrication
5.1 | Assemble material components as per drawing.
5.2 | Dimensional check & fit up inspection prior to welding
5.3 | Welding of assembled components
5.4 | Ongoing visual weld inspection of all welded components.
6 | Inspection & Testing
6.1 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc
6.2 | Piping. NDE in accordance with approved drawings, specifications
6.3 | Structural. NDE of lifting lugs in accordance with drawings/specifications (100%)
6.4 | Weld Repairs
6.5 | Hydrotest
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 3 of 4
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Concrete | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Darren Duthie
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-003
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
7 | Offsite Surface Treatment
7.1 | Grit blast and prime
7.2 | Complete applicable surface treatment
8 | Assembly & Verification
8.1 | Structural, Mechanical and Piping completion and verification
8.2 | Punch listing completed
9 | Dispatch
9.1 | Review completed ITP
9.2 | Preparation & packaging for transport & load out to site
9.3 | Delivery to Site
9.4 | MDR (Compiled Progressively)
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev A |  | Page 4 of 4
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Earthworks | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-003
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
|  |  | PRIMERO |  |  |  | FORTESCUE METALS GROUP LTD.
Name: (print)
Position Title
Signature
Date
INSPECTION AND TEST PLAN 02704-ITP-CI-001
INSPECTION AND TEST PLAN 02704-ITP-CI-003
INSPECTION AND TEST PLAN 02704-ITP-CI-003
INSPECTION AND TEST PLAN 02704-ITP-CI-003
INSPECTION AND TEST PLAN 02704-ITP-CI-003

## ITP-004
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 1 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | - Structural | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger |  |  |  | - Mechanical
|  | Final Release/Responsibility by: | [6 empty] | - Piping | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [6 empty] | Installation | Client Doc No.:
(ONSITE)
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Design/Specifications
1.1 | Review Drawings and Data Sheets
2 | Approvals |  |  |  |  | AFC Drawings
2.1 | Submit Project Documentation, ITP etc
3 | Materials |  |  | AFC Drawings |  | AS-1379 | NATA Test Results
3.1 | Inspect materials a per Material Control Procedure
3.2 | Check for imperfections in flanges such as gouges and or protrusions in the serrations of gasket seating faces.
3.3 | Check the correct materials are installed in piping spools as specification and line class
3.4 | Store materials and welding consumables to eliminate damage and segregate Stainless Steel to prevent contamination.
3.5 | Check supply of vendor equipment for completeness
4 | Concrete Pre Cast Installation |  |  | 100-SP-CI-0003 |  | AFC Drawings | ITR 203, ITR-204
4.1 | Earthworks methods and compaction information received and verified against design
4.2 | Excavated levels checked against design
4.3 | Bedding sand or fines added where required, thickness not to exceed 50mm
4.4 | Inspect Pre-cast footings for defects and tolerances
4.5 | Pre-cast footings landed and postion confirmed
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 2 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Concrete | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Darren Duthie
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
5 | Structural Installation | [5 empty] | ACRS Certificates
5.1 | Anchor bolts and foundations checked (Location/Elevation/Level)
5.2 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required)
5.3 | Erect Primary columns and beams following grid lines including vertical bracing.
5.4 | Structure Installed and checked (Location/Elevation/Level) Snug tighten Primary connections throughout the structure Complete Primary steel pre-tension survey
5.5 | Tension all primary steel bolts and nuts
5.6 | Complete primary steel post-tension survey
5.7 | Grouting
5.8 | Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports Complete Secondary steel pre-tension survey
5.9 | Tension all secondary steel bolts and nuts
5.1 | Complete secondary steel post-tension survey
5.11 | Grating and handrails to be installed as required to ensure safe work practice and access.
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 3 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Concrete | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Darren Duthie
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
6 | Mechanical Installation |  |  | 0 |  | AFC Drawings | ITR 203, ITR-204
6.1 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter and the entire grouting surface scabbled
6.2 | Check that the levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of mechanical equipment.
6.3 | Land equipment and confirm tie in points are within tolerance
6.4 | Confirm piping tie-ins are complete and grout equipment. Check and verify grouting is acceptable
6.5 | Check alignment of drive/couplings Rotation Checked
6.6 | Couplings Bolted, torqued and checked
6.7 | V-Belts, or Chain drives installed and checked Safety guards installed and checked
6.8 | Ensure no stress on nozzles from piping connection
6.9 | Preservation & Maintenance
6.1 | Ensure preservation and maintenance as per manufacturer recommendation
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev 0 |  | Page 4 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Concrete | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Darren Duthie
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
7 | Piping |  |  | 0 |  | AFC Drawings | ITR 203, ITR-204
7.1 | Pre-Processing and Assembly
7.1.1 | Material allocation, Transfer & marking of heat numbers. Mark piping material to required length. Cut pipe sections to length in readiness for Preparation, bevelling.
7.1.2 | Assembly of components prior to welding. Check: Fit-up & alignment, Root Gap & Landing, Install pipe Supports as per Drawing.
7.1.3 | Dimensional check prior to welding.
7.1.4 | Welding (Field)
7.1.5 | Ensure Internals are clean and dry before welding.
7.1.6 | Welding to be performed by qualified welder in accordance with approved welding Procedure Specification.
7.1.7 | Carry out Welding of Joints , Field welds, Pipe supports & attachments.
7.1.8 | Welding visual Inspection, Check: Root pass/weld size/profile & finish Closing weld size/profile & finish Traceability records to be maintained, Welder, WPS Consumables etc.
7.1.9 | Weld repairs (if any) remove defect and re-weld in accordance with qualified procedure.
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev A |  | Page 5 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Earthworks | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
7.2 | Inspection and Testing
7.2.1 | Dimensional check of piping assembly after welding "As Built"
7.2.2 | 100% Final visual inspection of all welds and traceability check.
7.2.3 | Non Destructive Examination:
7.2.4 | Carry out required Non Destructive Examination (NDE) as per Client specification requirements. Extent of, as per applicable to the appropriate "AS4041 Class piping " and Piping line lists.
7.3 | Pipe Installation - Bolted Joints
7.3.1 | Inspect nozzle integrity on all static and rotating equipment to which pipe spools are connected.
7.3.2 | Ensure Internals are clean and dry prior to assembly.
7.3.3 | Shim steelwork at pipe support locations and survey for correct elevation.
7.3.4 | Assembly - Install pipework Align mating flange joints to specified tolerances - To mechanical equipment. - To static equipment. - pipe to pipe.
7.3.5 | Install in line piping components gaskets, nuts, bolts and Instrumentation.
7.3.6 | Check valves & instrumentation for Identification tags & check orientation. install valves and instrumentation.
7.3.7 | Ensure correct bolts are installed & tensioned.
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev A |  | Page 6 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Earthworks | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
7.4 | Pressure Testing and Treatment
7.4.1 | Develop Hydrostatic or Pneumatic Pressure Test Packs. Check NDE & Calibration Certificates prior to testing.
7.4.2 | Flush clean piping system. The cleaning media shall be as per testing media detailed on the line List.
7.4.3 | Pressure Test Pipework 'Witness Test for any leaks'.
7.4.4 | Verification of cleanliness & dryness.
7.4.5 | Chemically Clean and Pickle piping of scale, contaminants and stains
8 | Surface Treatment (Touch Ups) |  |  | 0 |  | AFC Drawings | Batch Docket
8.1 | Protect surfaces not requiring treatment, e.g. Field welds. nameplates. machined surfaces.
8.2 | Check the blast medium is to the specifications.
8.3 | Check surface cleaning as per specification
8.4 | Monitor atmospheric conditions daily for Temperature (> 5 •c and <50 •c) and Humidity (>20% and <85%)
8.5 | Check item to be painted (piping I steelwork etc.) for defects, damage. No welding flux, splatter, sharp edges etc. Confirm all inspections, NOT etc. on the item have been completed prior to painting.
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev A |  | Page 7 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Earthworks | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
REF | INSPECTION AND TEST ACTIVITY |  |  | APPLICABLE DOCUMENT OR PROCEDURE ETC. |  | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT |  |  | INSPECTION AND VERIFICATION
[10 empty] | Primero |  | Client |  | 3rd Party Inspection
[10 empty] | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
8.6 | Ensure the items to be painted are adequately laid out and masked as needed
8.7 | Check correct paint is being used
8.8 | Ensure paints are mixed as per manufacturers recommendation
8.9 | Check application is correct and is free of paint runs and other defects
9 | Final Inspection on Completion | [5 empty] | Manufacturer's TDS
9.1 | -Carry out final inspection -Generate punch list -Verification / clearance of punch list
10 | Finalise Documentation
10.1 | Progressively check all test reports are correct.
10.2 | Sign off Inspection & Test Plan.
10.3 | MDR to be progressively compiled and submitted to client for final approval.
LEGEND |  | H = HOLD POINT |  |  | ACT = ACTIVITY |  |  | R/A = REVIEW & APPROVE DOC. |  |  |  | D = DIMENSIONAL INSPECTION
|  | S = SUBMIT DOCUMENT TO CLIENT |  |  | W = WITNESS POINT |  |  | V = VISUAL INSPECTION |  |  |  | V/S = VERIFYING SIGNATURE
|  | M = MONITOR ON A RANDOM BASIS |  |  | W @ R = WITNESS @ RANDOM |  |  | A = APPROVE |  |  |  | R & C = REVIEW & COMMENT
CLIENT: |  | FMG Solomon |  |  |  |  | DOCUMENT |  | I.T.P. | Rev A |  | Page 8 of 8
PROJECT: |  | CLIENT REFERENCE No: |  |  |  |  | SCOPE OF ITP: |  | Earthworks | Primero Job No: |  |  | 2704
|  | Prepared By: |  |  | Peter Kroeger
|  | Final Release/Responsibility by: | [7 empty] | Primero Doc No.: |  |  | 02704-ITP-CI-004
|  | CLIENT APPROVAL | [7 empty] | Client Doc No.:
|  |  | PRIMERO |  |  |  | FORTESCUE METALS GROUP LTD.
Name: (print)
Position Title
Signature
Date
INSPECTION AND TEST PLAN 02704-ITP-CI-001
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004
INSPECTION AND TEST PLAN 02704-ITP-CI-004