| Client: |  |  |  |  |  |  | Contract No: |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Project: |  |  |  |  |  |  | Document No: |  |  |  |  |  |  |  | Revision: |  |  |  |  |
| Area/System No: |  |  |  |  |  |  | Area/System Description: |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Document |  |  |  |  |  | Controlling Document |  |  |  |  |  |  |  | Verifying Documents |  |  |  |  |  |
| No. | Title |  |  |  |  | No. |  | Title |  |  |  |  |  | No. |  |  | Title |  |  |
|  | BGER Project Quality Management Plan (PQMP) |  |  |  |  | AS/NZS 3000 |  | Wiring rules |  |  |  |  |  |  |  |  | Material certificates |  |  |
|  | Mobilisation, education and training procedure |  |  |  |  |  |  | Client’s specifications |  |  |  |  |  |  |  |  | Tools calibration certificates |  |  |
|  | Punch list procedure |  |  |  |  |  |  | AFC Dawings |  |  |  |  |  |  |  |  | Electrical equipment list |  |  |
|  | As built procedure |  |  |  |  |  |  | 3D model |  |  |  |  |  |  |  |  | Equipment datasheet |  |  |
|  |  |  |  |  |  | AS/NZS 1742.3 |  | Manual of uniform traffic control devices Traffic control for works on roads |  |  |  |  |  |  |  |  | Client’s ITRs |  |  |
|  |  |  |  |  |  | IEEE 837 |  | Standard for Qualifying Permanent Connections Used in Substation Grounding |  |  |  |  |  |  |  |  | Delivery Packing List |  |  |
|  |  |  |  |  |  | AS/NZS 3100 |  | Approval and test specification — General requirements for electrical equipment |  |  |  |  |  |  |  |  | Material Inspection Report |  |  |
|  |  |  |  |  |  | AS/NZS 3012 |  | Electrical installations - Construction and demolition sites |  |  |  |  |  |  |  |  | Training register |  |  |
|  |  |  |  |  |  | AS/NZS 3760 |  | In-service safety inspection and testing of electrical equipment and RCDs |  |  |  |  |  |  |  |  |  |  |  |
| Legend |  |  |  |  |  |  |  |  |  |  | Approval and Change History |  |  |  |  |  |  |  |  |
| Verification Activity |  |  |  |  |  |  |  |  |  |  | Rev | Details |  | Date |  | Prepared by (BGER) |  |  | Client Approval (XXX) |
| H – Hold Point |  |  | Work shall not proceed past the Hold Point until released by the Organisation imposing the Hold Point. 48 hrs. notice required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| W – Witness Point |  |  | An Inspection Point that may be witnessed by the Organisation imposing the Witness Point. 48 hrs. notice required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I – Inspection |  |  | Formal inspection activity to be undertaken and recorded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| S – Surveillance |  |  | An activity that is subject to on-going monitoring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| R – Review |  |  | Review of text reports/records or other evidence of compliance. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Responsible Person (RP) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUP |  |  | Supervisor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QR |  |  | Quality Representative (Project Engineer) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUR |  |  | Surveyor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Item | Activity/Operations/Stage No. | Controlling Document/ Procedure | Standard, Spec, Drawing Ref or Acceptance Criteria | Verifying Document/ Report/ Certificate | Verification Activity by |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | BGER RP | BGER/ sign | Client/ sign |  |
| 1.0 | Approvals |  |  |  |  |  |  |  |
| 1.1 | Prepare BGER’s ITP and submit to Client for Approval | PQMP | ITP | Approved ITP | QR | H | H |  |
| 1.2 | Confirm correct competent person, training, qualification and VOC’s are correct | PQMP | Mobilisation, education and training procedure | Training register | SUP | H | H |  |
| 1.3 | Prepare clearing permit | PQMP | Environmental Management Plan | Approved clearing Permit | SUP | H | H |  |
| 1.4 | Approved and issued permission for excavations | PQMP | All relevant permissions obtained | Approved ITP Excavation permission | SUP | H | H |  |
| 1.5 | Ensure traffic management plan is current and associated warning signs, flagging, barriers, etc are in place | PQMP | AS/NZS 1742 Client’s project procedure | Approved traffic management plan | SUP | H | H |  |
| 2.0 | Material Receipt |  |  |  |  |  |  |  |
| 2.1 | Check material for damage due to delivery and fabrication defect | PQMP | AFC Drawing | Delivery Packing List, Material Inspection Report | QR | I, R | R |  |
| 2.2 | Confirm correct material received | PQMP | Client’s specs | Material Certificates | QR | I, R | R |  |
| 2.3 | Check that correct quantities and dimensions of material and consumables are delivered | PQMP | AFC Drawing, Bill of Material | Material Inspection Report, Electrical consumables material certificates | QR | I, R | R |  |
| 2.4 | Ensure all test equipment is calibrated and registered. Ensure all construction equipment and tooling are tested and correct tag is in place. | PQMP | Control of test equipment procedure AS/NZS 3012 AS/NZS 3760 | Calibration and records register | SUP | I, R | S |  |
| 2.5 | Confirm cable drums to be used have been identified as tested on drum before use and are placed in stable position | PQMP | Drum ‘PASS’ identification | Drum ITR | SUP | I, R | R |  |
| 2.6 | At the trench site, verify correct conduit for the task as per underground drawings | PQMP | AFC Drawing | Client’s ITR | SUP | I, R | R |  |
| 3.0 | Scope Of Work |  |  |  |  |  |  |  |
| 3.1 | For underground, verify trench is dug to correct EL and sloped as per drawing, verified with survey. Trench is shored or benched for safety, trench sand bedding free from any sharp objects and compacted along the full length of trench | PQMP | AFC Drawing Client’s specs 3D model Excavating, Trenching and Penetrations procedure | Client’s ITR | SUP/ SUR | I, R | R |  |
| 3.2 | Confirm the conduit and pit are installed as per design and all ends have no shape edges, ensure earth pit lids are accessible | PQMP | AFC Drawing | Client’s ITR | SUP | I, H | R |  |
| 3.3 | Confirm the exothermic and crimped joint for earth grid are as per design | PQMP | AFC Drawings IEEE 837 | Client’s ITR | SUP | H | H |  |
| 3.4 | Verify back fill and compact in correct manner | PQMP | Excavating, Trenching and Penetrations procedure | Client’s ITR | SUP | I | R |  |
| 3.5 | For aboveground, verify cable route is clear and correct as per design | PQMP | AFC Drawings 3D model | Client’s ITR | SUP | I | R |  |
| 3.6 | Verify cable-pulling device in safe position and all cable pulled to correct tension as per manufacturer’s specifications | PQMP | Manufacturers specification | Client’s ITR | SUP | I | S |  |
| 3.7 | Cable length to be verified and recorded before cutting | PQMP | Cable schedule | Client’s ITR | SUP | H | S |  |
| 3.8 | Survey cables, ensure joints are approved and cables have been tested before the backfill of trench | PQMP | Client’s specs Excavating, Trenching and Penetrations procedure | Client’s ITR | SUP | I | R |  |
| 3.9 | Confirm earth electrode connections are clean, tight, secure, and coated with protective coating | PQMP | Client’s specs | Client’s ITR | SUP | I | R |  |
| 3.10 | Confirm drilled earth rods depth and enhancing compounds are as per design | PQMP | Client’s specs | Client’s ITR | SUP | I | R |  |
| 3.11 | Survey cables, ensure joints are approved and cables have been tested before the backfill of trench | PQMP | Client’s specs Excavating, Trenching and Penetrations procedure | Client’s ITR | SUP | H | R |  |
| 3.12 | Confirm before connection that resistance check has been carried out to grid or local earth bar as necessary and that values of resistance are in compliance with project requirements | PQMP | Client’s specs AS/NZS 3000 AS/NZS 3100 | Client’s ITR | SUP | R | R |  |
| 3.13 | Confirm termination and connection is as per typical design drawing with mechanical and anti-oxidising protection as required. Underground connections are to be wrapped with Denso tape | PQMP | Client’s Specs | Client’s ITR | SUP | R | R |  |
| 4.0 | Inspection verification and finishing works |  |  |  |  |  |  |  |
| 4.1 | Test and/or inspect equipment as per section 3 above to manufacturer and project requirements or under technical direction of vendor representative as required | PQMP | Equipment datasheet Vendor manual Client’s specs AS/NZS 3000 | Client’s ITR | QR | H | H |  |
| 4.2 | Confirm complete compilation of all the Inspection & Test Records by discipline/system. This compilation will be added to the dossier for System/Area Mechanical Completion which when completed with all disciplines and other works will be submitted to Client for approval. | PQMP | Equipment datasheet Vendor manual Client’s specs AS/NZS 3000 | Client’s ITR | QR | R | S |  |
| 4.3 | Walk down, Inspection and Works to go list generated, rectified and closed out | PQMP | Punch list procedure | Works to go list | QR/SUP | I | S |  |
| 5.0 | Quality Documents |  |  |  |  |  |  |  |
| 5.1 | Verify sign off of all inspection and test documentation | PQMP | Signed ITRs | Construction verification | QR | H | H |  |
| 5.2 | Verify all drawings are complete and submitted “As built” status | PQMP | As-built procedure | As built register | QR | H | H |  |
| 5.3 | Completion of MDR | PQMP | Client’ Specs | MDR progressive review and sign off | QR | R | R |  |