## Register
INSPECTION AND TEST PLAN (ITP) REGISTER
|  | CLIENT : | Rio Tinto Iron Ore
|  | PROJECT : | Oily Water System Upgrade
|  | PROJECT No : | 01708
|  | SITE : | Cape Lambert
|  | LAST UPDATED : | 2014-09-28
ITR No. | Title |  |  | Originator | Date Issued | Date Completed
ITP-001 | STRUCTURAL, MECHANICAL AND PIPING SUPPLY AND FABRICATION – OFF SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-002 | STRUCTURAL, MECHANICAL AND PIPING INSTALLATION - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-003 | ELECTRICAL AND INSTRUMENTATION INSTALLATION - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-004 | EARTHWORKS |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-005 | CONCRETE WORKS |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-006 | CONCRETE PATCHING & REPAIR WORKS |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX

## ITP-001
ITP Number: |  | 01708-ITP-QM-001 | Client Contract Number: | PE600390/C/CC/1000 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Structural, Mechanical and Piping Fabrication - OFFSITE
Works Locations: |  | Fabrication Workshop
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.1 |  | 2: Review Scope of Work and associated specifications; 3: I; 4: Client SOW in Contract PE600390; 5: Client Specifications, refer Note 1; 6: Contract Document; 7: W
1.2 |  | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Client Specifications, refer Note 1; 6: AFC Drawings, VDDI; 7: W
2 |  | 2: APPROVALS
2.1 |  | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Client Specifications, refer Note 1; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
2.2 |  | 2: Submit Weld Procedure Specifications & Qualifications; 3: I; 4: WPS & WPQ Reports; 5: ASME IX; AS1554;; 6: Approved WPSs; 7: W
2.3 |  | 2: Submit Welder Qualifications; 3: I; 4: Welder Qualification Reports & register; 5: ASME IX; AS1554;; 6: Approved Welder Qualifications; 7: W
3 |  | 2: MATERIALS
3.1 |  | 2: Monitor Incoming Materials (New) And Client supply; 3: I; 4: Client MTO; AFC Drawings; 01708-LST-ME-001; 5: YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, refer Note 1; 6: Signed Delivery Dockets; Material Certificates, Inspection Certificates; 7: SV, W
3.2 |  | 2: Material Traceability; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications; 5: Materials Specifications; 6: Traceability Records for Piping Works; 7: SV
4 |  | 2: MATERIALS PREPARATION
4.1 |  | 2: Mark materials for cutting & weld preparation. Dimensional check.; 3: S; 4: Piping Isometrics & structural detail drawings; 5: AFC Drawings; 6: AFC Drawings, 01708-ITR-ME-008; 7: SV
4.2 |  | 2: Prepare controlled/cut materials for fabrication; 3: S; 4: Material Control procedure, 01708-PLN-PM-002; 5: Client Specifications, refer Note 1; 6: AFC Drawings, 01708-ITR-ME-008; 7: SV
4.3 |  | 2: Consumables Control; 3: S; 4: Consumable Control Procedure, 01708-PLN-PM-002; 5: Client Specifications, refer Note 1, and ASME IX, AS1554; 6: Manufacturers Recommendations; 7: SV
5 |  | 2: FABRICATION
5.1 |  | 2: Assemble material components as per drawing.; 3: S; 4: AFC Drawings; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: AFC Drawings; 7: SV
5.2 |  | 2: Dimensional check & fit up inspection prior to welding; 3: S; 4: Dimensional check procedure, 01708-PLN-PM-002; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: AFC Drawings – isometric & fabrication detail drawings; 7: SV
5.3 |  | 2: Welding of assembled components; 3: S; 4: Weld/Welder Traceability documentation:; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: Approved WPS’s; 01708-ITR-ME-008; 7: SV
5.4 |  | 2: Ongoing visual weld inspection of all welded components.; 3: S; 4: Client Specifications, WPS; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: 01708-ITR-ME-008; 7: SV
6 |  | 2: INSPECTION & TESTING
6.1 |  | 2: Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc; 3: I; 4: Dimensional check procedure, 01708-QA-PRO-003; 5: Client Specifications, refer Note 1; AS 4041; AS 1554;; 6: AFC Drawings – isometric & fabrication detail drawings; 7: SV
6.2 |  | 2: Piping. NDE in accordance with approved drawings, specifications; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001; 5: Client Specifications, refer Note 1; AS 4041; Normal Fluid Service;; 6: Certified NATA reports;01708-ITR-ME-008; 7: SV
6.3 |  | 2: Structural. NDE of lifting lugs in accordance with drawings/specifications (100%); 3: S; 4: NDE Procedures; YSP-0000-SPE-S-002; 5: Client Specifications, refer Note 1; AS 1554;; 6: Certified NATA reports;01708-ITR-ME-008; 7: SV
6.4 |  | 2: Weld repairs; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001, YSP-0000-SPE-S-002; 5: Client Specifications, refer Note 1; AS 1554;; 6: Certified NATA reports;01708-ITR-ME-008; 7: H
6.5 |  | 2: Hydrotest; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001, YSP-0000-SPE-S-002; 5: Client Specifications, refer Note 1; AS 1554;; 6: Certified NATA reports;01708-ITR-ME-008; 7: H
7 |  | 2: OFFSITE SURFACE TREATMENT
7.1 |  | 2: Grit blast and prime; 3: S; 5: Client Specifications, refer Note 1; 6: Surface Treatment Records; 7: SV
7.2 |  | 2: Complete applicable surface treatment; 3: S; 5: Client Specifications, refer Note 1; 6: Surface Treatment Records; 7: SV
8 |  | 2: ASSEMBLY & VERIFICATION
8.1 |  | 2: Structural, Mechanical and Piping completion and verification; 3: S; 4: Construction Methodolgy (Schedule M of the Contract); 5: Client Specifications, refer Note 1; 6: AFC Drawings & Specifications; 7: SV
8.2 |  | 2: Punch listing completed; 3: S; 4: Construction Methodolgy (Schedule M of the Contract); 5: Client Specifications, refer Note 1; 6: AFC Drawings, Punchlist & Specifications; 7: H
9 |  | 2: DESPATCH
9.1 |  | 2: Review completed ITP; 3: I; 4: 01708-ITP-QA--001; 5: Client Specifications, refer Note 1; 6: Approved ITP; 7: SV, R
9.2 |  | 2: Preparation & packaging for transport & load out to site; 3: I; 4: Inspection release form; 5: Primero Form; 6: Delivery Documentation; 7: W, H
9.4 |  | 2: Delivery to Site; 3: I; 4: Inspection release – review & acceptance; 5: Primero Form; 6: Inspection Acceptance form; 7: W, H
9.5 |  | 2: MDR (Compiled Progressively); 3: I; 4: Manufacturers Data Report; 5: Client Specifications, refer Note 1; 6: Approved MDR; 7: W
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: SS-C110, SS-C111, SS-C118, SS-M101, SS-M112, SS-M118, SS-M119, SS-M120, SS-M190, SS-P120
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-002
ITP Number: |  | 01708-ITP-QM-002 | Client Contract Number: | PE600390/C/CC/1000 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | B | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Structural, Mechanical and Piping Installation - ON-SITE
Works Locations: |  | OILY WATER SEPERATOR
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.2 |  | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Client Specifications, refer Note 1; 6: AFC Drawings; 7: W
2 |  | 2: APPROVALS
2.1 |  | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Client Specifications, refer Note 1; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
3 |  | 2: MATERIALS
3.1 |  | 2: Inspect materials a per Design IFC drawings; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1. Data Sheets; 6: Delivery Dockets, Material Register & Certificates, Consumable Certificates, Data Sheets; 7: H
3.2 |  | 2: Check for imperfections in flanges such as gouges and or protrusions in the serrations of gasket seating faces.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: SS-M120; 6: Applicable ITR's; 7: H/R
3.3 |  | 2: Check the correct materials are installed in piping spools as specification and line class; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AS 4041, SS-M120; 6: Applicable ITR's; 7: H/R
3.4 |  | 2: Store materials and welding consumables to eliminate damage and segregate Stainless Steel to prevent contamination.; 3: I; 4: Material Control Procedure; 5: Client Specifications, refer Note 1; 7: SV
4 |  | 2: STRUCTURAL INSTALLATION; 3: I
4.1 |  | 2: Anchor bolts and foundations checked (Location/ Elevation/ level); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings Client Specifications, refer Note 1; 6: Visual Inspection or Survey Report where required. Handover certificate from concrete contractor; 7: R
4.2 |  | 2: Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required); 3: I; 4: Construction Methodology; 5: Australian Standards and Regulations; 6: Certification Approved Lift Study Report where required; 7: H
4.4 |  | 2: Structure Installed and checked (Location/ Elevation/ level) Snug tighten Primary connections throughout the structure Complete Primary steel pre-tension survey; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: Visual Inspection or Survey Report where required
4.5 |  | 2: Tension all primary steel bolts and nuts; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: 01708-ITR-ME-015; 7: W
4.6 |  | 2: Complete primary steel post-tension survey; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: Visual Inspection or Survey Report where required; 7: H
4.7 |  | 2: Grouting; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: 01708-ITR-ME-014
4.8 |  | 2: Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports Complete Secondary steel pre-tension survey; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: 01708-ITR-ME-006, Survey Report
4.9 |  | 2: Tension all secondary steel bolts and nuts; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: 01708-ITR-ME-015, Survey Report; 7: W
4.10 |  | 2: Complete secondary steel post-tension survey; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: Survey Report; 7: H
4.11 |  | 2: Grating and handrails to be installed as required to ensure safe work practice and access.; 3: I; 4: Construction Methodology; 5: Approved Drawings Client Specifications, refer Note 1; 6: 01708-ITR-ME-006, Survey Report; 7: W
5 |  | 2: MECHANICAL INSTALLATION; 3: I
5.1 |  | 2: Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter and the entire grouting surface scabbled; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01708-ITR-ME-014, Survey Report; 7: H
5.2 |  | 2: Check that the levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of mechanical equipment.; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01708-ITR-ME-011, Survey Report; 7: H
5.3 |  | 2: Land equipment and confirm tie in points are within tolerance; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: Survey Reports
5.4 |  | 2: Confirm piping tie-ins are complete and grout equipment. Check and verify grouting is acceptable; 3: I; 4: Client Specifications, refer Note 1 Manufacturers directions; 5: AFC Drawings, Vendor IOM; 6: Material Safety Data Sheets (MSDS), 01708-ITR-ME-013 or 01708-ITR-ME-014; 7: H
5.5 |  | 2: Check alignment of drive/couplings Rotation Checked; 3: I; 4: Client Specifications, refer Note 1 Manufacturers directions; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01708-ITR-ME-011, Vendor IOM; 7: H & R
5.6 |  | 2: Couplings Bolted, torqued and checked; 3: I; 4: Client Specifications, refer Note 1 Manufacturers directions; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01708-ITR-ME-011, Vendor IOM; 7: H
5.7 |  | 2: V-Belts, or Chain drives installed and checked Safety guards installed and checked; 3: I; 4: Client Specifications, refer Note 1 Manufacturers directions; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01708-ITR-ME-011, Vendor IOM; 7: H
5.8 |  | 2: Ensure no stress on nozzles from piping connection; 3: I; 4: Client Specifications, refer Note 1 Manufacturers directions; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01708-ITR-ME-011, cold spring check; 7: W
6 |  | 2: PIPING
6.1 |  | 2: Pre Processing and Assembly
6.1.1 |  | 2: Material allocation, Transfer & marking of heat numbers. Mark piping material to required length. Cut pipe sections to length in readiness for Preparation, bevelling.; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: Isometrics/Cutting List; 7: SV
6.1.2 |  | 2: Assembly of components prior to welding. Check: Fit-up & alignment, Insertion depth into fitting, Install pipe Supports as per Drawing.; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: Isometrics/Cutting List; 7: H
6.1.3 |  | 2: Dimensional check prior to crimping.; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings; 6: Isometrics/Cutting List; 7: H
6.1.5 |  | 2: Ensure Internals are clean and dry before Crimping; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: 01708-ITR-ME-003; 7: SV
6.1.7 |  | 2: Carry out Crimping of Joints; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: Visual Inspection; 7: H
6.1.8 |  | 2: Crimping visual Inspection, Check: roundness and crimp profile, depth of joint pentration; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: 01708-ITR-ME-019; 7: SV
6.1.9 |  | 2: Crimp repairs (if any) remove defect and re-crimp in accordance with qualified procedure.; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: 01708-ITR-ME-019; 7: H
6.2 |  | 2: Inspection and Testing
6.2.1 |  | 2: Dimensional check of piping assembly after welding "As Built"; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: As-Built Drawings; 7: H
6.2.2 |  | 2: 100% Final visual inspection of all crimping and traceability check.; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: 01708-ITR-ME-019, 'As Built' Drawings; 7: H
6.2.3 |  | 2: Non Destructive Examination:; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.2.4 |  | 2: Carry out required Non Destructive Examination (NDE) as per Client specification requirements. Extent of, as per applicable to the appropriate "AS4041 Class piping " and Piping line lists.; 3: I; 4: AFC Drawings Tubepress Installation guidelines Client Specifications, refer Note 1; 5: AFC Drawings Tubepress Installation guidelines; 7: H
6.3 |  | 2: Pipe Installation - Bolted Joints
6.3.1 |  | 2: Inspect nozzle integrity on all static and rotating equipment to which pipe spools are connected.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-001; 7: W
6.3.2 |  | 2: Ensure Internals are clean and dry prior to assembly.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-001; 7: H
6.3.3 |  | 2: Shim steelwork at pipe support locations and survey for correct elevation.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-001, Visual Inspection or Survey results; 7: H/R
6.3.4 |  | 2: Assembly - Install pipework Align mating flange joints to specified tolerances - To mechanical equipment. - To static equipment. - pipe to pipe.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-001, Isometrics; 7: H
6.3.5 |  | 2: Install in line piping components gaskets, nuts, bolts and Instrumentation.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-001, Isometrics, Material certificates; 7: H
6.3.6 |  | 2: Check valves & instrumentation for Identification tags & check orientation. install valves and instrumentation.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: P&ID's; 7: W
6.3.7 |  | 2: Ensure correct bolts are installed & tensioned.; 3: I; 4: AFC Drawings Client Specifications, refer Note 1; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-001, Isometrics, Torque Wrench Calibration Report; 7: R
6.4 |  | 2: Pressure Testing
6.4.1 |  | 2: Develop Hydrostatic Pressure Test Packs. Check NDE & Calibration Certificates prior to testing.; 3: S; 4: Hydrostatic Test Procedure Client Specificaitons; 5: AS 4041 Client Specificaitons, refer Note 1; 6: System Test Pack; 7: H
6.4.2 |  | 2: Flush clean piping system. The cleaning media shall be as per testing media detailed on the line List.; 3: S; 4: Hydrostatic Test Procedure Client Specificaitons; 5: AS 4041 Client Specificaitons, refer Note 1; 6: PGr PressureTest Report; 7: W
6.4.3 |  | 2: Pressure Test Pipework 'Witness Test for any leaks'.; 3: S; 4: Hydrostatic Test Procedure Client Specificaitons; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-005; 7: H
6.4.4 |  | 2: Verification of cleanliness & dryness.; 3: I; 4: Hydrostatic Test Procedure Client Specificaitons; 5: AS 4041 Client Specificaitons, refer Note 1; 6: 01708-ITR-ME-005; 7: W
7 |  | 2: SURFACE TREATMENT (TOUCH UPS)
7.1 |  | 2: Protect surfaces not requiring treatment, e.g. Field welds. nameplates. machined surfaces.; 3: S; 4: SS-P120, Client Specifications; 5: SS-P120; 6: Visual Inspection; 7: SV
7.2 |  | 2: Check the blast medium is to the specifications.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.3 |  | 2: Check surface cleaning as per specification; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.4 |  | 2: Monitor atmospheric conditions daily for Temperature (> 5 •c and <50 •c) and Humidity (>20% and <85%); 3: S; 5: SS-P120; 6: Visual Inspection or Bureau of Meteorology Data; 7: SV
7.5 |  | 2: Check item to be painted (piping I steelwork etc.) for defects, damage. No welding flux, splatter, sharp edges etc. Confirm all inspections, NOT etc. on the item have been completed prior to painting.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: H
7.6 |  | 2: Ensure the items to be painted are adequately laid out and masked as needed; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.7 |  | 2: Check correct paint is being used; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions, AFC drawings; 5: SS-P120; 6: Visual Inspection; 7: SV
7.8 |  | 2: Ensure paints are mixed as per manufacturers recommendation; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.9 |  | 2: Check application is correct and is free of paint runs and other defects; 3: I; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: DFT report; 7: SV
8 |  | 2: FINAL INSPECTION ON COMPLETION
8.1 |  | 2: -Carry out final inspection -Generate punch list -Verification / clearance of punch list; 3: I; 4: 01708-E1-001 QMP, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Field Inspection Checklist (FIC) 's Completions database; 7: H
9 |  | 2: FINALISE DOCUMENTATION
9.1 |  | 2: Progressively check all test reports are correct.; 3: I; 4: 01708-E1-001 QMP, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Reviewed and Approved ITR's; 7: H
9.2 |  | 2: Sign off Inspection & Test Plan.; 3: I; 4: 01708-E1-001 QMP, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: ITP; 7: R
9.3 |  | 2: MDR to be progressively compiled and submitted to client for final approval.; 3: I; 4: 01708-E1-001 QMP, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: MDR; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: SS-C110, SS-C111, SS-C118, SS-M101, SS-M112, SS-M118, SS-M119, SS-M120, SS-M190, SS-P120
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-003
ITP Number: |  | 01708-ITP-QM-003 | Client Contract Number: | PE600390/C/CC/1000 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Electrical & Instrumentation Supply and Installation - ON-SITE
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: Site Preparation, Planning and Inspection; 3: I; 4: 01708-SWI-HS-093 Site Preparation, Planning and Inspection; 5: 01708-SWI-HS-093 Site Preparation, Planning and Inspection; 6: N/A
2 |  | 2: Installation of Cable Ladders and Trays; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-SWI-HS-091 Installation of Cable Tray and Cable Ladder 01708-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-SWI-HS-091 Installation of Cable Tray and Cable Ladder 01708-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01708-ITR-EL-033 Cable Tray - Ladder; 7: R
3 |  | 2: Installation of Below Ground Conduits; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-SWI-HS-094 Trenching, Excavating, Pot Holing 01708-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-SWI-HS-094 Trenching, Excavating, Pot Holing 01708-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01708-ITR-EL-036 Underground Cable Installation; 7: W, R
4 |  | 2: Installation of Aboveground Rigid Discontinuous Conduit; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01708-ITR-EL-034 Above Ground Conduit; 7: R
5 |  | 2: Installation of Cables and Fibre Optic Cables; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-SWI-HS-092 Installation of Cables 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-SWI-HS-092 Installation of Cables 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-001 On Drum Testing for Cables 01708-ITR-EL-002 Cable Installation 01708-ITR-EL-036 Underground Cable Installation; 7: W, R
6 |  | 2: Installation of Electrical Earthing; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-015 Electrical Earthing; 7: W, R
7 |  | 2: Installation of Kiosk; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-011 Distribution Board Installation; 7: R
8 |  | 2: Testing and Termination Cables; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-003 Cable Test 01708-ITR-EL-004 Cable Termination; 7: R
9 |  | 2: Installation of Local Control Stations; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-030 Local Control; 7: R
10 |  | 2: Installation of Lighting and lighting Poles; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-029 Lighting; 7: R
11 |  | 2: Installation of Control Panels; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-023 Control Panel; 7: R
12 |  | 2: Installation of Equipment Pre Installation; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-IN-003 Equipment Pre-Installation Verification; 7: R
13 |  | 2: Installation of Instruments; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-IN-001 Instrument Installation 01708-ITR-IN-003 Equipment Pre-Installation Verification; 7: R
14 |  | 2: Installation of Instrument Tubing; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-IN-006 Instrument Tubing Installation; 7: R
15 |  | 2: Installation of Pressure Safety Valves; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-IN-002 Pressure Relief Valve Preinstallation; 7: W, R
16 |  | 2: Instrument Loop Checks; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-IN-007 Instrument Loop Check; 7: R
17 |  | 2: Installation of Electrical Motors; 3: I; 4: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 5: 01708-PRO-EL-005 Inspection Test Record Procedure 01708-PRO-EL-004_A Electrical ITR Matrix Procedure 01708-PRO-EL-002_A Electrical Testing and Reporting Procedure 01708-PRO-EL-007 Calibration and Equipment Procedure; 6: 01708-ITR-EL-017 Electrical Motor Installation; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: SS-E101, SS-E104, SS-E110, SS-E115, SS-E120, SS-E123, SS-E124, SS-E125, SS-E153, SS-E155, SS-E156 & SS-E159
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-004
ITP No. |  | 01708-ITP-QM-004 |  |  | INSPECTION AND TEST PLAN
Revision: A |  |  |  |  | EARTHWORKS
Location: |  |  | Cape Lambert | [5 empty] | Activity: | Earthworks | [6 empty] | References: |  |  | RTIO SS-C101 Earthworks
Lot Number: | [8 empty] | Process: | Oily Water Seperator | [6 empty] | Prepared by: |  |  | Scott McCormack
Date: | [8 empty] | Description: | [7 empty] | Approved by: |  |  | Grant Brinkmann
|  |  |  | VERIFICATION | [6 empty] | TESTING |  |  |  |  | INSPECTION | [5 empty] | RECORDS & COMMENTS
ITEM NO | OPERATIONAL ACTIVITIES |  |  | Specification Reference |  |  | Acceptance Criteria |  |  |  | Test / Inspection Method | Test / Inspection Method |  | Test / Inspection Frequency |  | PGr |  | Sign & Date | RTIO |  | Sign & Date
1 | Preliminaries
1.1 | Authorised documentation for commencement of new work is in place. |  |  | PGr Quality Plan RTIO Contract |  |  | Documentation received and approved by Superintendant. |  |  |  | SE to review with PM. |  |  | Once (Pre Start) prior to commencing. |  | PM (H) |  |  | SR (H)
2 | Pre Commencement Activities
2.1 | Safety. |  |  | PGr Project HSE MP |  |  | Safety Measures in place as per Safety Management Plan, Job specific JSEA completed and signed off by relevant parties. |  |  |  | PGr SE to Verify. |  |  | Prior to start of works. |  | SE (R)
2.2 | Environment. |  |  | PGr Project HSE MP |  |  | Environmental control in place as per Project Environmental Management Plan |  |  |  | PGr SE to Verify. |  |  | Prior to start of works. |  | SE (R) |  |  | SR (S)
2.3 | Traffic Management. |  |  | PGr Project Traffic Management Plan |  |  | Traffic Management control in place and any permits/ approvals available. |  |  |  | PGr SE to Verify. |  |  | Prior to start of works |  | SE (R) |  |  | SR (S)
2.4 | Survey Set-Out. |  |  | Design Drawings |  |  | Survey Offset pegs in place showing extent of excavations |  |  |  | PGr SE to Verify. |  |  | Prior to start of works. |  | SE (R) |  |  | SR (S)
2.5 | RTIO Permit to Dig. |  |  | RTIO SS-C101-6.4 |  |  | Permit to dig provided by Superintendent. |  |  |  | PGr SE to Verify. |  |  | Prior to commencement of each excavation not already covered by a permit. |  | PE (H) |  |  | SR (H)
2.6 | PGr Excavation Permit |  |  | Excavation Permit. |  |  | Excavation permit (including site excavation report if excavation is greater than 1.5m) completed & signed onto by all involved in works. |  |  |  | PGr SE to Verify. |  |  | Prior to commencement of each excavation not already covered by a permit. |  | SE (H)
3 | General
3.1 | Lot Identification |  |  | Lot Register |  |  | Area is identified by a unique lot |  |  |  |  | Records Complete |  | At Start Up |  | SE (R)
4 | Construction
4.1 | Excavation – Geotech |  |  | RTIO SS-C101-8 |  |  | All areas where fill material has been placed by PGr on top of ground previously prepared by the earthworks contractor shall be subject to testing. |  |  |  |  | Samples taken and tested by NATA approved laboratory. |  | Yet to be determined by Superintendent. |  | SE (H)
4.2 | Excavation |  |  | RTIO SS-C101-8 |  |  | Inspection shall be undertaken to ensure excavation carried out to the dimensions shown on the drawings, sufficient room is allowed for the erection and removal of formwork and that no unsuitable material is present. |  |  |  |  | RTIO SS-C101-8 |  | Each Excavation. |  | SE (H) |  |  | SR (W)
4.3 | Stabilisation of Excavation |  |  | RTIO SS-C101-8 |  |  | Excavation greater then 1.5m above base of excavation. Battered faces of excavation to be battered at max 1:1 and benching 1m x1m or shoring to be in place. Or it can be assessed as stable by a competent person |  |  |  |  | Visual. |  | Each Excavation. |  | SE (S)
4.4 | Excavation – Surface Inspection |  |  | RTIO SS-C101-8 |  |  | Superintendent to inspect excavation and confirm material is suitable for bearing purposes. |  |  |  |  | Superintendent Inspection. |  | Each Excavation. |  | SE (H) |  |  | SR (H)
4.5 | Backfill – Prior to Placement |  |  | RTIO SS-C101-13 |  |  | Before backfilling has commenced all silt, rubbish & foreign material shall be removed from the excavation and backfill shall not be placed against concrete which is less than 48 hours old. Concrete surface finish shall be in accordance with PGr Concrete patching works prior to backfill. |  |  |  |  | Visual. |  | Each Lot |  | SE (IP)
4.6 | Backfill Material – Selection |  |  | RTIO SS-C101-11 |  |  | Excavation backfilled with suitable fill material. |  |  |  |  | PGr SE to Verify. |  | Each Excavation. |  | SE (H) |  |  | SR (R)
4.7 | Inspection – Prior to Placement of Backfill |  |  | RTIO Spec. Part 7.5 |  |  | Excavation to be cleared of all foreign materials and dewatered. The superintendant shall inspect areas prior to placement of fill material. |  |  |  |  | PGr SE to Verify. |  | Each Excavation. |  | SE (H) |  |  | SR (H)
4.8 | Lean-Mix Blinding |  |  | RTIO SS-C107 Design Drawings |  |  | A Layer of, Grade S15 blinding shall be placed under all footings a shown on the contract design drawings. |  |  |  |  | PGr SE to Verify. |  | Each Excavation. |  | SE (H) |  |  | SR (S)
4.9 | Cement Treated Type A – Materials |  |  | RTIO SS-C107 & SS-C108 Design Drawings |  |  | Materials to be as per quality plan and Superintendent to approve mix design prior to placing order. Details of mixing plant, location, retarder and cement binder to be noted on delivery dockets. |  |  |  |  | Visual/test results. |  | Each Lot. |  | SE (R) |  |  | SR (S)
4.10 | Backfill Material – Placement & Compaction |  |  | RTIO SS-C101-11 |  |  | Backfill shall be placed in layers not exceeding 230mm loose thickness and compacted to not less than 95% MMDD under concrete footings and 92.5% MAD elsewhere. |  |  |  |  | Visual / Test Results. |  | Each Excavation. |  | SE (IP) |  |  | SR (S)
SYMBOLS & ABBREVIATIONS: | [5 empty] | INSPECTION CODES:
LA | Local Authority |  |  |  |  | (S) |  | Surveillance Point |  | PM - Project Manager |  |  | SE - Site (QA) Engineer |  | SF - Supervisor / Foreman
PGr | Primero Group |  |  |  |  | (W) |  | Witness Point |  | PE - Project Engineer |  |  | SA - Safety Advisor |  | QM - Quality Manager
RTIO | Riotinto |  |  |  |  | (H) |  | Hold Point |  | S- Survey |  |  | SR - Site / Client Rep
[6 empty] | (R) |  | Review

## ITP-005
ITP No. |  | 01708-ITP-QM-005 |  |  | INSPECTION AND TEST PLAN
Revision: A |  |  |  |  | CONCRETE WORKS
Location: |  |  | Cape Lambert | [5 empty] | Activity: | Concrete Installaton | [6 empty] | References: |  |  |  | RTIO SS-C107 Concrete Supply RTIO-SS-C108 Structural Concrete
Lot Number: | [8 empty] | Process: | Oily Water Seperator | [6 empty] | Prepared by: |  |  |  | Scott McCormack
Date: | [8 empty] | Description: | [7 empty] | Approved by: |  |  |  | Grant Brinkmann
|  |  |  | VERIFICATION | [6 empty] | TESTING |  |  |  |  | INSPECTION | [6 empty] | RECORDS & COMMENTS
ITEM NO | OPERATIONAL ACTIVITIES |  |  | Specification Reference |  |  | Acceptance Criteria |  |  |  | Test / Inspection Method | Test / Inspection Method |  | Test / Inspection Frequency |  | PGr |  | Sign & Date |  | RTIO |  | Sign & Date
1 | Preliminaries
1.1 | Authorised documentation for commencement of new work is in place, incl. design of falsework and formwork submitted to RTIO for review. |  |  | PGr Quality Plan. RTIO Specifications Contract document |  |  | Documentation received and approved by Superintendant. |  |  |  |  | SE to review with PM. |  | Once (Pre Start) prior to commencing. |  | PM (H) |  |  | SR (H)
1.2 | Concrete Mix Design. |  |  | RTIO SS-C107 Design drawings |  |  | Concrete Mix Design Approved by Superintendant. |  |  |  |  | PGr SE to review. |  | Once (prior to ordering concrete of each design type). |  | SE (H) |  |  | SR (H)
1.3 | Form Release Agent, Surface Retardant, Curing Compound. |  |  | RTIO SS-C108-7.4 |  |  | Material selection approved by Superintendent. |  |  |  |  | PGr SE to review |  | Once (prior to commencemen of formwork). |  | SE (H) |  |  | SR (R)
1.4 | Reinforcement – Supply. |  |  | RTIO SS-C108-53 |  |  | Copies of the reinforcement supplier’s certification that reinforcing complies to AS4671 & ACRS. Certificates shall be included in MDR |  |  |  |  | PGr SE to review. |  | Once (Prior to procurement of reinforcement). |  | SE (H) |  |  | SR (R)
1.5 | Reinforcement Schedules. |  |  | RTIO SS-C108-8 Design drawings |  |  | RTIO supplied with one complete set of reinforcement schedules. |  |  |  |  | PGr PE to review. |  | Prior to placement of each scheduled area of reinforcement. |  | PE (R) |  |  | SR (S)
1.6 | Falsework & Formwork Design | [5 empty] | Design of falsework and formwork to be received & reviewed by Project Engineer. |  |  |  | SE to review with PE. |  |  | Prior to commencement of construction of each lot of formwork. |  | SE (R)
2 | Pre Commencement Activities
2.1 | Pre- Start Meeting |  |  | Daily Pre-start Checklist. |  |  | Pre-Start Meeting completed prior to start of works. |  |  |  | Pre-Start Meeting Record Complete. |  |  | Prior to start of works. |  | SE (R)
2.2 | Safety |  |  | PGr Project Safety Plan |  |  | Safety Measures in place as per Project Safety Plan. |  |  |  | SE to review with Site Supervisor |  |  | Prior to start of works. |  | SE (R)
2.3 | Environment |  |  | PGr Project Environmental Plan |  |  | Environmental control in place as per Project Environmental Plan |  |  |  | SE to review with Site Supervisor |  |  | Prior to start of works. |  | SE (R) |  |  |  | SR (S)
2.4 | Traffic Management |  |  | PGr Project Traffic Management Plan |  |  | Traffic Management control in place and any permits/approvals available. |  |  |  | Verify |  |  | Prior to start of works |  | SF (R) |  |  |  | SR (S)
3 | General
3.1 | Lot Identification |  |  | Lot Register |  |  | Area is identified by a unique lot. |  |  |  | SE to ensure records are complete. |  |  | On commencement of each lot. |  | SE (R)
4 | Construction
4.1 | Setting out |  |  | PGr Work Procedure |  |  | The structure must be set out by a surveyor prior to the placement of formwork and reinforcement. |  |  |  | Survey |  |  | Each Lot |  | SF (S) |  |  |  | SR (I)
4.2 | Preparation of Ground Under Slabs. |  |  | RTIO Spec.. Part 15.1 |  |  | Builders Film (Waterproof Membrane) is present and intact under all slabs. Or Blinding concrete is in situ |  |  |  | Visual. |  |  | Prior to construction of Reinforcement & Immediately prior to placement of concrete. |  | SE (W) |  |  |  | SR (I)
4.3 | Preparation of Lean Mix Blinding Under Pad Footings. |  |  | PGr Work Procedure |  |  | Blinding surface is clean, free from foreign substances and thoroughly wetted immediately prior to placement of concrete. |  |  |  | Visual. |  |  | Immediately prior to placement of concrete. |  | SE (S) |  |  |  | SR (I)
4.4 | Preparation of Construction Joints. |  |  | RTIO SS-C108 PGr Work Procedure |  |  | Construction joints to be suitably scabbled. Construction joint surface is clean, free from foreign substances and thoroughly wetted immediately prior to placement of concrete. |  |  |  | Visual. |  |  | Prior to construction of reinforcement & Immediately prior to placement of concrete. |  | SE (S) |  |  |  | SR (I)
4.5 | Formwork - Placement |  |  | RTIO SS-C108-7 PGr Work Procedure |  |  | Formwork to be placed as per survey set out and accurately and safely secured. Formwork shall not be placed in locations where reinforcement and other elements cannot be inspected. Prior to placing reinforcement a release agent has been applied to the face of the formwork compatible with the required surface finish. |  |  |  | Visual |  |  | Prior to closing of formwork. |  | SE (S)
4.6 | Formwork Placement – Prefabricated |  |  | RTIO SS-C108-7 PGr Work Procedure |  |  | Prefabricated Formwork to be dimensionally checked by a engineer or surveyor prior to being lifted into position. |  |  |  | Survey |  |  | Upon completion of formwork construction & prior to installation. |  | SF (S)
4.7 | Formwork Inspection |  |  | RTIO SS-C108-7 PGr Work Procedure |  |  | Formwork has been constructed in accordance with the submitted formwork design, is clean, to correct lines and levels and will result in required surface finish being met. |  |  |  | Visual. |  |  | Upon completion of formwork construction. |  | SE (S) |  |  |  | SR (I)
4.8 | Reinforcement – Handling and Storage |  |  | RTIO SS-C108-8 PGr Work Procedure |  |  | Reinforcement shall be clean and free from dust, oil, grease etc. |  |  |  | Visual. |  |  | SF to inspect prior to placement. |  | SF (S)
4.9 | Setting out of Reinforcement |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | The structure must be set out by a surveyor prior to the placement of reinforcement. |  |  |  | Survey |  |  | Each Lot |  | (SCP) |  |  |  | SR (I)
4.10 | Welding of Reinforcement |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | Details of any welded joint other than those specifically nominated on the design drawings are to be submitted to the Superintendents Representative prior to welding. Welding not to take place unless approval for welded joints has been received. Approved welding to be in accordance with AS1554.3 |  |  |  | Verify. |  |  | Verify |  | SE (H/S) |  |  |  | SR (H/S)
4.11 | Reinforcement – Installation |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | Reinforcement to have minimum clear cover as shown as shown on the drawings, and to be within tolerances |  |  |  | Visual. |  |  | Prior to closing formwork & prior each pour. |  | SE (W) |  |  |  | SR (S)
4.12 | Reinforcement – Supports |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | Plastic chairs or mortar block spacers shall be used for reinforcement supports. Mortar block spacers shall have properties at least equal to the surrounding concrete. |  |  |  | Visual. |  |  | Prior to closing formwork & prior each pour. |  | SE (W) |  |  |  | SR (S)
4.13 | Cast-Ins / Block-outs – Planning |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | Cast-Ins to be checked on plans prior to pours. |  |  |  | Verify |  |  | Each Lot. |  | SE (H) |  |  |  | SR (W)
4.14 | Cast-Ins / Block-outs – Placement |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | Cast-ins shall be within tolerances 3mm nominated in the specifications & design drawings. Position and fastening to be checked prior to placement of concrete. |  |  |  | Survey / Visual. |  |  | Once embedded items have been fixed in position, prior to placement of concrete. |  | SE (H) |  |  |  | SR (W)
4.15 | Reinforcement inspection |  |  | RTIO SS-C108-8 PGr Work Procedure Design drawings |  |  | PGr to carry out inspection ensuring reinforcement meets design specification. |  |  |  | Survey / Visual. |  |  | Each Lot. |  | SE (IP)
4.16 | Concrete Placement – General |  |  | RTIO SS-C108-9 PGr Work Procedure Design drawings |  |  | A pre-pour notice form (see appendix B of Specification) shall be filled out and submitted to the Superintendent giving 24 hours notice of the intention to place concrete. Work out of daylight hours shall only occur with consent by the Superintendents Representative. |  |  |  | Visual / Documentation Concrete Pour Checklist |  |  | Prior to placement of concrete. |  | SE (H) |  |  |  | SR (H)
4.17 | Concrete Placement – Weather Conditions |  |  | RTIO Spec.. Part 19.4 |  |  | Concrete shall not be placed when ambient temperature is lower than 5°C. Pours during adverse weather conditions shall not take proceed. Each pour to be assed and the Superintendents Representative and PGr Project Manager to be in agreement as to whether or not the pour is to continue. |  |  |  | SER to verify with PGr PM when conditions are adverse. |  |  | Prior to placing order for concrete. |  | SE / PM (H) |  |  |  | SR (S)
4.18 | Concrete mix |  |  | AS 3973, AS3600 RTIO SS-C107 |  |  | Concrete mix design shall be in accordance with the Project Specification. All dockets showing mix design ingredients shall be retained by PGr Site Engineer. |  |  |  | Verify / Testing. |  |  | Each Pour |  | SE (H) |  |  |  | SR (S)
4.19 | Concrete Slump |  |  | AS1012 RTIO SS-C107 |  |  | Concrete slump shall be As per the design specification / Quality Plan (80mm +/- 15mm). |  |  |  | Verify / Testing. |  |  | As per RTIO SS-C107 Pours 1-5m³ - 1 sample Pours 5-25m³ 1 2 samples (first batch & 1 other) Pours 25-50m³ 3 samples (first batch & 2 others at random) Pours 50-100m³ 4 samples (first batch & 2 others at random) Regardless of addition of plasticiser or other admixtures prior to placement. |  | SE (H) |  |  |  | SR (S)
4.20 | Concrete Placement – Concrete Temperature |  |  | RTIO SS-C107 |  |  | The temperature of concrete, measured immediately prior to placement, shall not be greater than 320C |  |  |  | Verify / Testing |  |  | As required. |  | SE (SCP) |  |  |  | SR (S)
4.21 | Concrete Placement – Discharge |  |  | RTIO SS-C108-10 |  |  | Concrete shall be incorporated into works within 60 minutes of batching. Discharge shall occur at a maximum drop height of 2m. |  |  |  | Verify |  |  | Every truck load. |  | SE (H) |  |  |  | SR (S)
4.22 | Concrete Placement – Construction Joint |  |  | RTIO SS-C108-10 |  |  | Construction Joints shall be moistened with a water or slurry mix prior to placement of concrete |  |  |  | Verify |  |  | All pours on construction joints or lean mix blinding. |  | SE (H) |  |  |  | SR (S)
4.23 | Concrete Placement – Compaction |  |  | RTIO SS-C108-10 |  |  | Vibration shall be applied to the full depth of each layer of concrete and extend into the top 150mm of the underlying layer. Concrete shall not be placed in layers exceeding 300mm. |  |  |  | Verify |  |  | Periodic observation of each pour. |  | SE (W) |  |  |  | SR (S)
4.24 | Concrete Placement – Surface Finish |  |  | RTIO SS-C108 |  |  | Surfaces of concrete shall have class 5 finish on unexposed surfaces. Exposed surfaces shall be of class 3 finish for vertical surfaces. Finish for Horizontal shall be finished with a non- slip finish as directed by the plans or superintendent. |  |  |  | Visual |  |  | All Formed Surfaces. |  | SE (H) |  |  |  | SR (S)
4.25 | Concrete Placement – Curing |  |  | RTIO SS-C108-10 |  |  | Concrete to be sufficiently cured using an approved curing compound as per the manufacturers specification. |  |  |  | Visual |  |  | All Surfaces. |  | SE (SCP) |  |  |  | SR (S)
4.26 | Concrete Testing |  |  | RTIO SS-C107 |  |  | All concrete testing must be to the frequencies set out in table 25.2 in the specification & section of this ITP. All records must be kept with relevant information and copies of all tests to be passed on to the superintendent within 7 days of the tests been completed. |  |  |  | Verify / Testing |  |  | As per RTIO SS-C107 Pours 1-5m³ - 1 sample Pours 5-25m³ 1 2 samples (first batch & 1 other) Pours 25-50m³ 3 samples (first batch & 2 others at random) Pours 50-100m³ 4 samples (first batch & 2 others at random) Regardless of addition of plasticiser or other admixtures prior to placement. |  | SE (R) |  |  |  | SR (R)
4.27 | Formwork Removal |  |  | RTIO SS-C108-7.6 |  |  | Formwork removed as per the references to left. |  |  |  | 24 hours (minimum) after placement of concrete |  |  | All Surfaces. |  | SE (W) |  |  |  | SR (S)
4.28 | Concrete Strength |  |  | AS 3600 |  |  | Concrete has reached specific 28 Day Design Strength according to NATA test lab results. |  |  |  | NATA test lab. |  |  | As per RTIO SS-C107 |  | SE (I) |  |  |  | SR (S)
4.29 | As Built - Tolerances |  |  | AS3600 Table 4.4.2 |  |  | Concrete, HD Bolts, embedded items etc. shall conform to the project drawings and specification and any changes to be noted on as constructed drawings & forwarded to RTIO. |  |  |  | Survey |  |  | Survey all elements. |  | SE (H) |  |  |  | SR (S)
4.30 | Defects |  |  | RTIO SS-108-12 |  |  | Defects to be marked on drawings and attached to ITP. For list of possible defects refer to RTIO spec |  |  |  | Visual. |  |  | Each Lot. |  | SE (H) |  |  |  | SR (W)
SYMBOLS & ABBREVIATIONS: | [5 empty] | INSPECTION CODES:
LA | Local Authority |  |  |  |  | (S) |  | Surveillance Point |  | PM - Project Manager |  |  | SE - Site (QA) Engineer |  | SF - Supervisor / Foreman
PGr | Primero Group |  |  |  |  | (W) |  | Witness Point |  | PE - Project Engineer |  |  | SA - Safety Advisor |  | QM - Quality Manager
RTIO | Riotinto |  |  |  |  | (H) |  | Hold Point |  | S- Survey |  |  | SR - Site / Client Rep
[6 empty] | (R) |  | Review

## ITP-006
ITP No. |  | 01708-ITP-QM-006 |  |  | INSPECTION AND TEST PLAN
Revision: A |  |  |  |  | CONCRETE PATCHING & REPAIR WORKS
Location: |  |  | Cape Lambert | [5 empty] | Activity: | Concrete Installaton | [6 empty] | References: |  |  | RTIO SS-C107 Concrete Supply RTIO-SS-C108 Structural Concrete
Lot Number: | [8 empty] | Process: | Oily Water Seperator | [6 empty] | Prepared by: |  |  | Scott McCormack
Date: | [8 empty] | Description: | [7 empty] | Approved by: |  |  | Grant Brinkmann
|  |  |  | VERIFICATION | [6 empty] | TESTING |  |  |  |  | INSPECTION | [5 empty] | RECORDS & COMMENTS
ITEM NO | OPERATIONAL ACTIVITIES |  |  | Specification Reference |  |  | Acceptance Criteria |  |  |  | Test / Inspection Method | Test / Inspection Method |  | Test / Inspection Frequency |  | PGr |  | Sign & Date | RTIO |  | Sign & Date
1 | Preliminaries
1.1 | Authorised documentation for commencement of new work is in place |  |  | PGr Quality Plan. RTIO Specs |  |  | Documentation received and approved by Superintendant. |  |  |  |  | SE to review with PM. |  | Once (Pre Start) prior to commencing. |  | PM (H) |  |  | SR (H)
1.2 | NCR to be raised for larger remedial works. |  |  | NCR |  |  | The NCR has been raised & submitted to RTIO complete with a proposed disposition. |  |  |  |  | Review. |  | Each Lot. |  | PE (H) |  |  | SR (H)
1.3 | Grout/Epoxy Products | [5 empty] | Product Accepted by RTIO |  |  |  |  | PGr SE to review. |  | Once (prior to ordering concrete of each design type). |  | SE (H) |  |  | SR (H)
2 | Pre Commencement Activities
2.1 | Pre- Start Meeting |  |  | Daily Pre-start Checklist. |  |  | Pre-Start Meeting completed prior to start of works. |  |  |  |  | Pre-Start Meeting Record Complete. |  | Prior to start of works. |  | SE (R)
2.2 | Safety |  |  | PGr Project Safety Plan. |  |  | Safety Measures in place as per Project Safety Plan. |  |  |  |  | SE to review with Site Supervisor |  | Prior to start of works. |  | SE (R)
2.3 | Environment |  |  | PGr Project Environmental Plan. |  |  | Environmental control in place as per Project Environmental Plan |  |  |  |  | SE to review with Site Supervisor |  | Prior to start of works. |  | SE (R) |  |  | SR (S)
2.4 | Repair Materials. |  |  | PGr Work Procedure Concrete Patching & Repair Work |  |  | Approval received from Superintendent for proposed repair materials. |  |  |  | PGr SE to Verify. |  |  | Each Lot |  | SE (R) |  |  | SR (S)
2.5 | Defective Works identified prior to remedial action. |  |  | PGr Work Procedure Concrete Patching & Repair Work |  |  | Remedial identified and covered by a repair procedure approved by Superintendent. |  |  |  | PGr SE to Verify. |  |  | Each Lot |  | SE (H) |  |  | SR (H)
3 | General
3.1 | Lot Identification. |  |  | Lot Register |  |  | Area is identified by a unique lot. |  |  |  | SE to ensure records are complete. |  |  | On commencement of each lot. |  | SE (R)
4 | Construction
4.1 | Surface Preparation. |  |  | PGr Work Procedure Concrete Patching & Repair Work. |  |  | Surface of Defect to be chipped to sound concrete. Area shall be brushed and cleaned to remove any loose material. |  |  |  | PGr SE to Verify |  |  | Each Lot |  | SE (W) |  |  | SR (S)
4.2 | Grout Preparation/ Placement. |  |  | MSDS Sheets/ Work Procedure/TDS. |  |  | Repair materials to be mixed and applied as per manufacturer specifications. |  |  |  | PGr SE to Verify |  |  | Each Lot |  | SE (S) |  |  | SR (S)
4.3 | Finishing. |  |  | PGr Work Procedure Concrete Patching & Repair Work. |  |  | Remedial work shall be finished such that the line and level are consistent with the surrounding concrete. |  |  |  | PGr SE to Verify. |  |  | Each Lot. |  | SE (H) |  |  | SR (H)
SYMBOLS & ABBREVIATIONS: | [5 empty] | INSPECTION CODES:
LA | Local Authority |  |  |  |  | (S) |  | Surveillance Point |  | PM - Project Manager |  |  | SE - Site (QA) Engineer |  | SF - Supervisor / Foreman
PGr | Primero Group |  |  |  |  | (W) |  | Witness Point |  | PE - Project Engineer |  |  | SA - Safety Advisor |  | QM - Quality Manager
RTIO | Riotinto |  |  |  |  | (H) |  | Hold Point |  | S- Survey |  |  | SR - Site / Client Rep
[6 empty] | (R) |  | Review