## Sheet1
ITP Discipline |  | Electrical and Instrumentation |  | Project Area | Donaldson Road Meter Station
Project Title |  | Donaldson Road Meter Station Upgrade |  | Revision | A
Primero Document No. |  | 06705-ITP-EL-001 |  | Date | 2018-05-21
Client |  | APA Group |  | Prepared
Client Document No. |  | YGP-020-ITP-QM-0005 |  | Approved | B. Zlnay
H = HOLD POINT |  | V = VISUAL INSPECTION | R = REVIEW | D = DIMENSIONAL INSPECTION |  | WR = WITNESS @ RANDOM
W = WITNESS POINT |  | M = MONITOR ON A RANDOM BASIS | A = APPROVE | S = SUBMIT DOCUMENT TO CLIENT
REF | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR PROCEDURE ETC. | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3RD Party Inspection
[5 empty] | Activity | Signature | Activity | Signature | Activity | Signature
1 | SPECIFICATIONS
1.1 | Review Scope of Work | YGP-SOW-A-0001 | Not Applicable | Contract Document | R |  | R
1.2 | Review Design | Packaged Equipment Specification, YGP-SP-A-0002 | YGP-SOW-A-0001 | Design Approval, VDS | S |  | R
1.3 | Review Drawings | AFC Drawings | Drawings | AFC Drawings | S |  | R
2 | MATERIALS
2.1 | Inspect materials | 00000-PRO-PC-002, AGW-SP-I-00002, 530-SP-J-0005 | Visual Checks | Delivery Dockets, Material Register & Certificates | V |  | R
2.2 | Store materials to eliminate damage | 00000-PRO-PC-002 | Visual Checks, Record of Storage Conditions | Material Register & Certificates | V |  | R
3 | ELECTRICAL AND INSTRUMENT INSTALLATION
3.1 | Prelimary Notice |  | Prelimary Notice sent to Energy Safety |  | S
3.2 | Pre-Installation Verification | 0000-PRO-EL-005 | Sight Documentation , Progressively file product data in MDR | Vendor IOM, Vendor Certificates, Vendor ITR’s / MDR | V |  | R
3.3 | Installation of Electrical Earthing | 00000-PRO-EL-005, 00000-PRO-EL-004, 00000‐PRO‐EL‐007, AGW-SP-I-00002, 530-SP-J-0005 | WA Electrical Requirements, AS3000 Wiring Rules, AS60079, Visual Checks As Per ITR, Main earthing conductors to be tested as less than 0.5 Ω, AS/NZS 3000 Clause 5.5.1, All Earthing Conductors connected to equipment are properly installed, protected and continuity tested to be less than 0.5 Ω | 06705-ITR-EL-107, 06705‐ITR‐EL‐127 | R,S |  | M
3.4 | Installation of Cable Ladders and Trays | 00000-PRO‐EL‐005, 00000-SPC-EL-001, 00000‐SWI‐HS‐091, 00000‐PRO‐EL‐004, AGW-SP-I-00002 | WA Electrical Requirements, AS3000 Wiring Rules, AS60079, Visual Checks As Per ITR | 06705-ITR-EL-123, As-built design data | V,M |  | R
3.5 | Installation of Rigid Discontinuous Conduit | 00000-SPC-EL-001, 00000‐PRO‐EL‐004, 00000‐PRO‐EL‐005 | WA Electrical Requirements, AS3000 Wiring Rules, AS60079, Visual Checks As Per ITR | 06705-ITR-EL-124, As-built design data | V,M |  | R
3.6 | Installation of Cables | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐SWI‐HS‐092, 00000‐PRO‐EL‐004, 00000‐PRO‐EL‐007, AGW-SP-I-00002, 530-SP-J-0005 | As per 3.4, AS3008, AS60079 | 06705-ITR-EL-129, As-built design data | V,M |  | R
3.7 | Testing and Termination Cables | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐PRO‐EL‐004, 00000‐PRO‐EL‐007, AGW-SP-I-00002, 530-SP-J-0005 | As per 3.4, Conductors and Armour must be less than 0.5Ω, Insulation Check must be greater than 10MΩ | 06705-ITR-EL-129 | V,M |  | R
3.8 | Installation of Junction Box Exe JB-004 | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐PRO‐EL‐004, 00000‐PRO‐EL‐007 | As per 3.5. | 06705-ITR-EL-116, 06705-ITR-EL-120 | V,M |  | R
3.9 | Installation of Heaters | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐PRO‐EL‐004, AGW-SP-I-00002, 530-SP-J-0005 | As per 3.5, check continuity of protective conductor earth fault loop impedance, check insulation resistance phase to earth, phase to phase & phase neutral, test voltage: 500 / 1000 vd.c. insulation test meter | 06705-ITR-EL-119, 06705-ITR-EL-121, 06705-ITR-EL-104 | V,M |  | R
3.1 | Construction of Control panels | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐PRO‐EL‐004 AGW-SP-I-00002 | Visual Checks as per ITR | 06705‐ITR‐EL‐115 | V,M |  | R
4.1 | Installation of Instruments | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐PRO‐EL‐004 AGW-SP-I-00002, 530-SP-J-0005 | As per 3.5. | 06705-ITR-IC-101, 06705-ITR-IC-103, 06705-ITR-IC-105, 06705-ITR-IC-109, 06705-ITR-IC-113, 06705-ITR-IC-114 | R,S |  | R
4.2 | Installation of Instrument tubing | 00000-SPC-EL-001, 00000‐PRO‐EL‐005, 00000‐PRO‐EL‐004 AGW-SP-I-00002, 530-SP-J-0005 | Gap gauge checks Pressurised snoop leak testing | 06705-ITR-IC-101, 06705-ITR-IC-103, 06705-ITR-IC-105, 06705-ITR-IC-109, 06705-ITR-IC-113, 06705-ITR-IC-114 | R,S |  | R
3.14 | Inspections of Electrical Equipment Installation in Hazardous Area (Gas) | 00000-SPC-EL-001, 00000-PRO-EL-003, Detailed Hazardous Area Inspection Procedure, 00000‐PRO‐EL‐004, 00000‐PRO‐EL‐005, AGW-SP-I-00002, 530-SP-J-0005 | As per 3.5. | Hazardous Area Verification Dossier including; a. All HA calculations, layouts b. Equipment drawings c. Equipment manuals d. Equipment HA certificates e. Detailed Inspection forms f. A custom cable inspection form for every cable terminating in a hazardous area g. A copy of the HA certifications for all personnel who conducted work in the hazardous area h. A signed letter from Primero Nominee acknowledging that the final installation meets all legal requirements, 06705-ITR-EL-128 i. Hazardous area equipment register listing all HA rated equipment used. k. HA schedule of release | R,S |  | A |  | H
4 | VERIFICATION
4.1 | Punchlisting | AFC Drawings, YGP-SOW-A-0001 | AFC Drawings, SOW | Completed Client Punchlist | H |  | H
5 | ENERGISATION
5.1 | Notice of Energisation | 00000-PRO-CM-001 | Notice of Energisation checklist 100% complete Polarity Test (upon no load Energisation) Fault Loop Impedance Test, RCD Tests on final Sub circuits, Visual indication / Loop check on instruments | Energy Safety Certificates and Notices, 06705-ITR-EL-201 | W |  | W
5.2 | Power up and hot loop testing of instruments | 00000-PRO-CM-001 | SOW | Energy Safety Certificates and Notices, 06705-ITR-EL-201 | W |  | H, W, A
5.2 | Heater Functional Testing | 00000-PRO-CM-001 | SOW | Energy Safety Certificates and Notices, 06705-ITR-EL-201 | W |  | H, W, A