## Register
INSPECTION AND TEST PLAN (ITP) REGISTER
|  | CLIENT : | Downer EDI
|  | PROJECT : | Roy Hill Diesel and Lube Farms
|  | PROJECT No : | 4204
|  | SITE : | Roy Hill
|  | LAST UPDATED : | 2014-01-28
ITR No. | Title |  |  | Originator | Date Issued | Date Completed
ITP-001 | STRUCTURAL, MECHANICAL AND PIPING SUPPLY AND FABRICATION – OFF SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-002 | STRUCTURAL, MECHANICAL AND PIPING INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-003 | ELECTRICAL AND INSTRUMENTATION INSTALLATION - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX

## ITP-001
ITP Number: | 05503-ITP-QA-003 | Client Contract Number: |  | Contract Item Number: |  | Legend : | R = Review | W=Witness | S = Surveillance
Revision Number: | 1 | Contractor Approval: | N/A | Equipment Number: | N/A |  | I =Inspection | H= Hold | A= Approval
Contractor: | Primero Group | Description of Service: | Electrical Upgrade
Works Locations: | Site
Task Number | Task Description | Location | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[6 empty] | Primero | Signature | BP | Signature
1 | ELECTRICAL AND INSTRUMENTATION WORK
1.1 | Installation of Conduits (Above and Under ground) | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS/NZS 2053 Conduits and Fittings for Electrical Installations Client's Installation Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 (Section-4) | ITR - Above ground Conduit (00000-ITR-EL-034) ITR - Underground Conduit (00000-ITR-EL-050) As-built design data | W |  | W,S
1.2 | Installation of Cable Tray/Ladder | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) Cable Schedule( D70029-09127-012-001[1]) | WA Electrical Requirements - Jan 2014 AS3000 Electrical Installation NEMA VE 1 CSA C22.2 No. 126.1 Metal Cable Tray Systems Client's Installation Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 (Section -4) | ITR - Cable Tray - Ladder (0000-ITR-EL-033) As-built design data | R |  | S
1.3 | Installation, Testing and Termination of Instrument / Control Cables/ Power Cables | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) Cable Schedule( D70029-09127-012-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS3008.1.1 Electrical Installations - Selection of Cables Client's Installation Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 (Section -2) | ITR - Cable Installation and Testing (00000-ITR-EL-049) As-built design data | R |  | S
1.4 | Installation of Electrical Earthing | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) | WA Electrical Requirements - Jan 2014 AS3000 Wiring Rules Client's Installation Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 (Section - 8) | ITR - Electrical Earthing (0000-ITR-EL-015) As-built design data | W |  | S
1.5 | Installation of Lighting - SW -303 - LJB-303 - YL-303A - YL-303B - SW-306 - YL-306 - LJB-304 - SW-304A - SW-304B - AL-304 - SW-305 - ML-305 | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) BP's Bill of Materials List (D70029-09127-011-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS3008 Electrical Installations (Selection of Cables) AS/NZS 1768 Lighting Protection Client's Inspection and Test Plans SOW - D70029-09127-019-002 (Section 1) Client's Installation Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 (Section - 8) | ITR - Lighting (00000-ITR-EL-029) As-built design data | R |  | S
1.6 | Installation of Instruments | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) Instruments as given in BP's Bill of Materials List (D70029-09127-011-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installations Client's Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 | ITR - Instrument Installation (0000-ITR-IN-001) As-built design data | R |  | S
1.7 | Installation of Electrical Equipment (In hazardous area) | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) Refer to BP's HAVD procedure | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS60079 Explosive Atmospheres "Gas" AS/NZS 4761 Guidelines for working with EEHA (Electrical Equipment in Hazardous Area) Explosion Protection Techniques for EPEE (Explosion Protected Electrical Equipment) and Hazardous Area i-e ANZEX, IECEx or Aus Ex | ITR - Initial Detailed Inspection for Hazardous Area Equipment (0000-ITR-EL-047) ITR - Initial Detailed Inspection for Hazardous Area Equipment (Common) (0000-ITR-EL-048) Hazardous Area Verification Dossier (Available upon request) As-built design data | H |  | W
1.8 | Installation of Transformer | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installations Client's Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 | ITR- Transformer Installation (00000-ITR-EL-028) As-built design data | W |  | S
1.9 | Installation of UPS-001 & DSB -001 | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installations Client's Specification for Electrical & Instrumentation Equipment SOW - D70029-09127-030-001 | ITR - UPS Installation (00000-ITR-EL-039_0) ITR- Distribution Board Installation 00000-ITR-EL-011 (Distribution Board Installation) | W |  | S
1.10 | Installation of Motor / Air Compressor | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) BP's Bill of Materials List (D70029-09127-011-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS60079 Explosive Atmospheres "Gas" AS/NZS 4761 Guidelines for working with EEHA (Electrical Equipment in Hazardous Area) Explosion Protection Techniques for EPEE (Explosion Protected Electrical Equipment) and Hazardous Area i-e ANZEX, IECEx or Aus Ex | ITR - Motor (0000-ITR-EL-006) ITR - Motor Cell Test (0000-ITR-EL-022) ITR - Local Control Station (0000-ITR-EL-030) As-built design data | R |  | S
1.11 | Installation of Misc Electrical Equipment (i-e Annunciator Panel, Remote I/O Panel) | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) BP's Bill of Materials List (D70029-09127-011-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS60079 Explosive Atmospheres "Gas" AS/NZS 4761 Guidelines for working with EEHA (Electrical Equipment in Hazardous Area) Explosion Protection Techniques for EPEE (Explosion Protected Electrical Equipment) and Hazardous Area i-e ANZEX, IECEx or Aus Ex | ITR - Misc Equipment (0000-ITR-EL-012) As-built design data | R |  | S
1.12 | Installation of Control Panels | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) BP's Bill of Materials List (D70029-09127-011-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS3008 Electrical Installations (Selection of Cables) Client's Specification for Control Panel Supply SOW - D70029-09127-030-002 | ITR - Control Panel (0000-ITR-EL-023) As-built design data | R |  | S
1.13 | Junction Box Installation | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) BP's Bill of Materials List (D70029-09127-011-001[1]) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installation AS3008 Electrical Installations (Selection of Cables) Client's Inspection and Test Plans SOW - D70029-09127-019-002 (Section - 6) | ITR - Inspection Test Record Procedure(00000-ITR-EL-025) As-built design data | R |  | S
1.14 | MCC1 /MCC2 Installation | BP Broome Terminal | Primero Inspection Test Record Procedure (0000-PRO-EL-005) | WA Electrical Requirements - Jan 2014 AS/NZS 3000 Electrical Installations AS3008 Electrical Installations (Selection of Cables) Client's Inspection and Test Plans SOW - D70029-09127-019-002 (Section -11 & 12) | ITR - LV Switchboard & MCC (00000-ITR-EL-020) ITR - BusBar (00000-ITR-EL-027) ITR - Energisation Report (00000-ITR-EL-045) As-built design data | H |  | W
2 | PRE-MOBILISATION DOCUMENTATION
2.1 | Section 9 of Client's SOW | Offsite | As per client's specifications - SOW | As per client's specifications - SOW | As per client's specifications - SOW
3 | TESTING AND TAGGING (Tooling etc)
3.1 | Testing and Tagging for all Construction Equipment and Tooling | BP Broome Terminal | As per client's specifications - SOW Appendix B | WA Electrical Requirements - Jan 2014 AS/NZS 3012 Constrcution Sites AS/NZS 3760 In Service Testing | 05503-REG-EL-001_0 Electrical Test and Tag Register | R
4 | FINALISATION
4.1 | Review completed ITP | BP Broome Terminal | ITP: BP 05503-ITP-QA-003_A Electrical | Client's Inspection and Test Plans SOW - D70029-09127-019-002 | Approved ITP | H |  | W
4.2 | Notice of Energisation | BP Broome Terminal | Notice of Energisation Procedure (00000-PRO-CM-001) | Notice of Energisation Procedure (00000-PRO-CM-001) | Energy Safety Certificates and Notices Primero Energisation Report (0000-ITR-EL-045) | H |  | W
4.3 | Site Acceptance Testing (SAT) & clearance of punch list | BP Broome Terminal | BP SAT ITP (D70029-09127-019-003) | Client's SOW Site Acceptance Testing (D70029-09127-019-003 ) Client's SOW Inspection and Test Plans (D70029-09127-019-002 ) (Section 14 - PunchList) | BP SAT ITP (D70029-09127-019-003) | H |  | W
GLOSSARY
| CONTROL | PRIMERO | BP
| APPROVAL | BP Approval required of the applicable activity or result from an activity
| HOLD | A critical operation or process beyond which work shall not proceed without attendance of the Primero representative | A critical operation or process beyond which work shall not proceed without attendance of the BP representative
| REVIEW | Review of documentation providing objective evidence of the suppliers compliance with contractual requirements | Review of documentation providing objective evidence of the suppliers compliance with contractual requirements
| WITNESS | A work activity to be witnessed by the Primero representative. The activity may proceed without the witness only with the prior written approval by the Primero representative | A work activity to be witnessed by the BP representative. The activity may proceed without the witness only with the prior written approval by the BP representative
| SURVEILANCE | Periodic surveillance by the Primero representative. No specific notification is required and the activity may proceed when the Primero representative is not present | Periodic surveillance by the BP representative. No specific notification is required and the activity may proceed when the BP representative is not present
| INSPECTION | A stage in the works where inspection and or testing is performed by personnel whose responsibility is to determine the acceptability of products or services and to record inspection and test data
Note on E15: Baila Shah: Request to be made for the dossier BP Document form 'FRM ANZ 12-07 01.doc' as mentioned on SOW page 33