## Sheet1
ITP Discipline |  | Ultra High Build Epoxy Coating |  | Project Area | Donaldson Road. Kwinana
Project Title |  | Donaldson Road Delivery Station Upgrade |  | Revision | A
Primero Document No. |  | 06705-ITP-ME-002 |  | Date | 2018-07-07
Client |  | APA Group |  | Prepared | R. O’Callaghan
Client Document No. |  | 18036-611-ITP-QM-0006 |  | Approved | B. Zlnay
H = HOLD POINT |  | V = VISUAL INSPECTION | R = REVIEW | D = DIMENSIONAL INSPECTION |  | WR = WITNESS @ RANDOM
W = WITNESS POINT |  | M = MONITOR ON A RANDOM BASIS | A = APPROVE | S = SUBMIT DOCUMENT TO CLIENT
REF | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR PROCEDURE ETC. | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3RD Party Inspection
[5 empty] | Activity | Signature | Activity | Signature | Activity | Signature
1 | SPECIFICATIONS
1.1 | Review Scope of Work | 18036-SOW-M-0003 | Not Applicable | Contract Document | R |  | R
1.2 | Review Design | Packaged Equipment Specification | 18036-SOW-M-0003 | Design Approval, VDS | S |  | R
1.3 | Supply all ITP’s, JSA, SWMS,MSDS & TDS | 530-SP-M-9601_2 | 530-SP-M-9601_2 | 06705-ITP-ME-002 | S |  | R
2 | Procure all equipment and resources for duration of works
2.1 | Procure all equipment and resources for duration of works | 530-SP-M-9601_2 | Compliance for Manufacture | Vendor MDR / Documentation | WR |  | WR / R
2.2 | Satisfy all OH&S, Quality & Environmental requirements. | APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 | APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 | MDR / Australian Standards
3 | PREPARE FOR COATING
3.1 | Dimensional check of pipe prior to surface treatment | 18036-ISO-P-0052.02_1 | 18036-ISO-P-0052.02_1 | 06705-ITP-ME-002 | V, D |  | M
3.2 | Inspect exposed pipe prior to commencement, Report any damage or suspect areas. | APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 | APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 | 06705-ITP-ME-002 | V |  | M
4 | SURFACE PREPARATION
4.1 | Abrasive Blast AS 1627.4 Class 2.5 75-100µm Profile The Abrasive shall be Garnet 30/60 Grit Surface shall be checked each day or each batch for Chloride contamination in accordance with AS3894.6 and shall be <25 mg/m³ Check weather conditions. record at least 3 times per day including prior to start, Air temp 10 C min, Surface temp 10 C min, Surface temp 3 C above dew point min, Relative humidity below 85% min | AS1627.4 AS3894.6 APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 Rev 0 Item 10.3 Surface Preparation | Class 2.5 75-100µm <25 mg/m³ | MDR Surface Treatment Records | M |  | M
4.2 | Measure surface profile using testex tape and dial calliper gauge record results and attach to Daily QA report. Surface profile is to be estimated in accordance with AS3894.5, The nominated surface profile shall be between 65-100 µm | AS1627.4 Class 2.5 AS3894.5 APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 Item 11 Inspection & Testing Item 11.3 Surface Profile | 65-100µm | MDR Surface Treatment Records | M |  | M
5 | APPLICATION OF SURFACE COATING
5.1 | Application of UHB via heated plural component spray unit and / or hand application. APA Group technical specification requires one coat application (1000-2000µm thickness) Total Thickness of both coats between 1000-2000µm (Ensure blasted pipe is coated within 4 hours) Ensure painters measure thickness at application using WFT gauge Check weather conditions. record at least 3 times per day including prior to start, Air temp 10 C min, Surface temp 10 C min, Surface temp 3 C above dew point min, Relative humidity below 85% min\ | Coating manufacturer TDS APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 Item 10.4 Application of Coating Item 10.4.3 Application | Min 1000 µm Max 2000 µm | MDR Surface Treatment Records | M |  | M
5.2 | Visually inspect pipe for defects runs, sags and inclusions. Repair if necessary - Check weather conditions. record at least 3 times per day including prior to start, Air temp 10 C min, Surface temp 10 C min, Surface temp 3 C above dew point min, Relative humidity below 85% min | APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 | APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 | MDR Surface Treatment Records | R, V |  | M
5.3 | Inspect total coated surfaces: DFT in accordance with AS3894 (1000-2000 µm ) Total Thickness Manually repair or Spray repair any defect or low areas as per requirements in APA Technical Spec, HOLIDAY TEST in accordance with AS3894 (6.3 kV) Manually Repair any defect or low areas. HARDNESS TEST in accordance with AS3894 (Shore D) Minimum Shore D > 85+/-2 As per item 5.3 in APA Technical Spec, The hardness of the cured coating shall be 85+/- 2 on the Shore D Hardness Scale ASTM D2240 Record and Repair any defects Repairing defects are limited to the specified conditions in APA Technical Spec. | Coating manufacturer TDS APA Group Spec. Buried Pipe Spec No.530-SP-M-9601_2 AS3894.3 AS3894.4 | AS3894, 530-SP-M-9601_2 | MDR Surface Treatment Records | W, V |  | W
5.4 | Preservation | Packaged Equipment Specification | Vendor Documents |  | M |  | M
5.5 | Verify that all internals are clean and dry. | 530-SP-M-9610_2 | 18036-SOW-M-0003 | 06705-ITR-ME-103 | M |  | M
6 | PREPARATION FOR HANDOVER
6.1 | Prepare all documentation for handover and sign off | Contract Document | 18036-SOW-M-0003 | All check sheets referenced, ITP to be signed off, As Built Drawings completed. | S |  | A