| Client: |  |  |  |  |  |  | Contract No: |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Project: |  |  |  |  |  |  | Document No: |  |  |  |  |  |  |  | Revision: |  |  |  |  |
| Area/System No: |  |  |  |  |  |  | Area/System Description: |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Document |  |  |  |  |  | Controlling Document |  |  |  |  |  |  |  | Verifying Documents |  |  |  |  |  |
| No. | Title |  |  |  |  | No. |  | Title |  |  |  |  |  | No. |  |  | Title |  |  |
|  | BGER Project Quality Management Plan (PQMP) |  |  |  |  | AS 1210 |  | Fired & Unfired Pressure Vessels |  |  |  |  |  |  |  |  | Material certificates |  |  |
| AS 4100 | Steel Structure |  |  |  |  | AS 3990 |  | Mechanical Equipment Steelwork |  |  |  |  |  | BGER-QA-CHL-0001 |  |  | Material Inspection Report |  |  |
|  | Weld Procedure Specifications (WPS) |  |  |  |  | AS 4041 |  | Pressure Piping |  |  |  |  |  |  |  |  | Survey Report |  |  |
|  | Welder Qualification Register (WQR) |  |  |  |  | AS 4100 |  | Steel Structures |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NDT Report |  |  |
|  |  |  |  |  |  |  |  | Manufacturer’s Specifications / IOM |  |  |  |  |  | BGER-QA-CHL-0002 |  |  | Coating & Surface Treatment Checklist |  |  |
|  |  |  |  |  |  |  |  | Client’s Specifications |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | AFC Dawings |  |  |  |  |  |  |  |  |  |  |  |
| Legend |  |  |  |  |  |  |  |  |  |  | Approval and Change History |  |  |  |  |  |  |  |  |
| Verification Activity |  |  |  |  |  |  |  |  |  |  | Rev | Details |  | Date |  | Prepared by (BGER) |  |  | Client Approval (XXX) |
| H – Hold Point |  |  | Work shall not proceed past the Hold Point until released by the Organisation imposing the Hold Point. 48 hrs. notice required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| W – Witness Point |  |  | An Inspection Point that may be witnessed by the Organisation imposing the Witness Point. 48 hrs. notice required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I – Inspection |  |  | Formal inspection activity to be undertaken and recorded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| S – Surveillance |  |  | An activity that is subject to on-going monitoring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| R – Review |  |  | Review of text reports/records or other evidence of compliance. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Responsible Person (RP) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUP |  |  | Supervisor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QR |  |  | Quality Representative (Project Engineer) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUR |  |  | Surveyor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NDTT |  |  | NDT Technician |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Item | Activity/Operations/Stage No. | Controlling Document/ Procedure | Standard, Spec, Drawing Ref or Acceptance Criteria | Verifying Document/ Report/ Certificate | Verification Activity by |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | BGER RP | BGER/ sign | Client/ sign |  |
| 1.0 | Approvals |  |  |  |  |  |  |  |
| 1.1 | Prepare BGER’s ITP submit to Client for Approval | PQMP | ITP | Approved Project Documentation | QR | H | H |  |
| 2.0 | Material Receipt |  |  |  |  |  |  |  |
| 2.1 | Check material for damage due to delivery and fabrication defect | PQMP | AFC Drawing, Delivery Packing List | Delivery Packing List, Material Inspection Report | QR | I, R | R |  |
| 2.2 | Confirm correct material received | PQMP | AFC Drawings | Delivery Packing List | QR | I, R | R |  |
| 3.0 | Preliminary Works |  |  |  |  |  |  |  |
| 3.1 | Prepare Lift Studies, if required, to suit and submit to Client for Approval. JHA in place and approved. | HSE Plan | HSE Plan | Lift Study, JHA | SUP/QR | R | R |  |
| 3.2 | Ensure all relevant concrete and steel documentation (survey reports etc) is complete and available for reference, conduct dimensional check. | AFC Drawings | AFC Drawings | Steel & Concrete ITRs/ITP Survey Report | SUP | H | R |  |
| 3.3 | Ensure hold down bolts correct (size, alignment, projection) | AFC Drawings | AFC Drawings | Survey Report | SUP | I | S |  |
| 3.4 | Check datum and foundation heights | AFC Drawings | AFC Drawings | Survey Report | SUP | I | S |  |
| 3.5 | Clean plinths and pockets, scabble plinths | AS 3600 |  |  | SUP | I | S |  |
| 4.0 | Mechanical Equipment Installation |  |  |  |  |  |  |  |
| 4.1 | Verify foundations and packing installed, if installing onto steelwork check condition of steel. |  |  | Survey Reports | SUP | I | R/S |  |
| 4.2 | Install mechanical equipment per the manufacturer’s recommendations | OEM IOM | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.3 | Verify location and dimensions correct | AFC Drawings | AFC Drawings | Mechanical Installation ITR | SUP | W | S |  |
| 4.4 | All drives and shafts aligned | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.5 | All belts and chain drives aligned, greased and adjusted to correct tension | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.6 | All pulleys and couplings assembled correctly | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.7 | All bearings correctly installed and greased, grease nipples/plugs installed | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.8 | Seals fitted correctly and all fasteners tightened. | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.9 | Valves and instrumentation fitted | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.10 | First fill oils complete | OEM IOM Client Specs | AFC Drawings, IOM | Mechanical Installation ITR | SUP | W | S |  |
| 4.11 | Complete grouting | Client specs | Client specs | Grouting ITR | SUP/QR | H | R |  |
| 5.0 | Surface Treatment |  |  |  |  |  |  |  |
| 5.1 | Touch up paint and surface paint as required | PQMP | Client’s specification | Coating & Surface Treatment Checklist | QR | W | R | Sub-contractor to supply detailed ITP |
| 6.0 | Final Inspection |  |  |  |  |  |  |  |
| 6.1 | Inspect equipment for correct installation and identify any damage, repair damage in accordance with OEM recommendations | PQMP | AFC Drawings, IOM | Mechanical Installation ITR | SUP/QR | H | S |  |
| 6.2 | Complete walk down with Client, identify any outstanding works and generate punchlist | PQMP | AFC Drawings, Client specs | Punchlist | SUP/QR | H | W |  |
| 6.3 | Complete any outstanding punchlist items to acceptable standard | PQMP | AFC Drawings, Client specs | Punchlist, Handover document | SUP/QR | H | W |  |
| 7.0 | Mechanical Completion |  |  |  |  |  |  |  |
| 7.1 | Confirm complete compilation of all the Inspection & Test Records by discipline/system. This compilation will be added to the dossier for System/Area Mechanical Completion which when completed with all disciplines and other works will be submitted to Client for approval. | PQMP | Client’s specification | Compilation of Inspection & Test Records | QR | R | S |  |
| 8.0 | Quality Documents |  |  |  |  |  |  |  |
| 8.1 | Completion of MDR | PQMP | Client’s specification | MDR progressive review and sign off | QR | R | R |  |