## ITP-REG
DISCIPLINE | ITP NO. | ITP TITLE | Origanator
EARTHWORKS | ITP-101 | Roads, Yards & Paving
EARTHWORKS | ITP-102 | Earthworks
CIVIL | ITP-201 | Bases & Pedestals
CIVIL | ITP-202 | Fences & Gates
CIVIL | ITP-203 | Stormwater & Oilywater
CIVIL | ITP-204 | Concrete
STRUCTURAL | ITP-301 | Platforms
STRUCTURAL | ITP-302 | Skids
STRUCTURAL | ITP-303 | Walkways
STRUCTURAL | ITP-304 | Structural Steel (Construction)
STRUCTURAL | ITP-305 | Structural Steel (Fabrication)
STRUCTURAL | ITP-306 | STRUCTURAL STEEL (Surface Treatment)
MECHANICAL | ITP-401 | Golden Weld
MECHANICAL | ITP-402 | Joint Integrity
MECHANICAL | ITP-403 | Seal welds
MECHANICAL | ITP-404 | Vessels
MECHANICAL | ITP-405 | Columns
MECHANICAL | ITP-406 | Towers
MECHANICAL | ITP-407 | Pumps (Centrifugal)
MECHANICAL | ITP-408 | Pumps (Sliding Vane)
MECHANICAL | ITP-409 | Compressors
MECHANICAL | ITP-410 | Fans
MECHANICAL | ITP-411 | Heat Exchangers
MECHANICAL | ITP-412 | Tanks
MECHANICAL | ITP-413 | Gas turbines
MECHANICAL | ITP-414 | Generators
MECHANICAL | ITP-415 | Mechanical Equipment
PIPING | ITP-501 | Pipe Fabrication
PIPING | ITP-502 | Piping Protective Coatings
PIPING | ITP-503 | Piping (in test pack & reinstatement pack)
PIPING | ITP-504 | Piping Installation
PIPING | ITP-505 | Piping - underground
ARCHITECTURAL | ITP-601 | Buildings
ELECTRICAL | ITP-701 | Main Site
ELECTRICAL | ITP-702 | Site Setup
ITP-801 |  | Indirects

## ITR-REG
|  |  |  | ITR No. | Title
Earthworks | [5 empty] | PMA-BHP-QC-TST-0125/ PR18015-900-QCR-1700-1001 | Excavation and Backfill
[6 empty] | PMA-BHP-QC-TST-0126/ PR18015-900-QCR-1700-1002 | Reinforcement Checklist
[6 empty] | PMA-BHP-QC-TST-0127/ PR18015-900-QCR-1700-1003 | Formwork Checklist
[6 empty] | PMA-BHP-QC-TST-0128/ PR18015-900-QCR-1700-1004 | Concrete Supply Checklist
[6 empty] | PMA-BHP-QC-TST-0129/ PR18015-900-QCR-1700-1005 | Concrete Foundation Preparation and Pour
[6 empty] | PMA-BHP-QC-TST-0130/ PR18015-900-QCR-1700-1006 | Concrete Record
[6 empty] | PMA-BHP-QC-TST-0131/ PR18015-900-QCR-1700-1007 | Precast Units
[6 empty] | PMA-BHP-QC-TST-0132/ PR18015-900-QCR-1700-1008 | Building and Civil Works
[6 empty] | PMA-BHP-QC-TST-0133/ PR18015-900-QCR-1700-1009 | Survey/ Acceptance for Concrete Structures
[6 empty] | PMA-BHP-QC-TST-0134/ PR18015-900-QCR-1700-1010 | Roadworks
[6 empty] | PMA-BHP-QC-TST-0135/ PR18015-900-QCR-1700-1011 | Civil Works - Storm Water Drainage
[6 empty] | PMA-BHP-QC-TST-0136/ PR18015-900-QCR-1700-1012 | Grouting Pre Pour Inspection and Application
[6 empty] | PMA-BHP-QC-TST-0137/ PR18015-900-QCR-1700-1013 | Fences and Gates
[6 empty] | PMA-BHP-QC-TST-0138/ PR18015-900-QCR-1700-1014 | Paving
[6 empty] | PMA-BHP-QC-TST-0136/ PR18015-900-QCR-1700-1012 | Grouting Pre Pour Inspection and Application
[6 empty] | PMA-BHP-QC-TST-0139/ PR18015-900-QCR-1800-1001 | Site Installation and Assembly
[6 empty] | PMA-BHP-QC-TST-0140/ PR18015-900-QCR-1800-1002 | High Strength Bolting
[6 empty] | PMA-BHP-QC-TST-0141/ PR18015-900-QCR-1800-1003 | Equipment Erection Survey Report
[6 empty] | PMA-BHP-QC-TST-0142/ PR18015-900-QCR-1800-1004 | Structural Alignment of Beams
[6 empty] | PMA-BHP-QC-TST-0143/ PR18015-900-QCR-1800-1005 | Structural Alignment of Columns
[6 empty] | PMA-BHP-QC-TST-0144/ PR18015-900-QCR-1800-1006 | Steel Structures Final inspection
Civil | ITR-201 |  |  |  |  | PMA-BHP-QC-TST-0145/ PR18015-900-QCR-1800-1007 | Structural Steel - Workshop Fabrication
| ITR-202 |  |  |  |  | PMA-BHP-QC-TST-0146/ PR18015-900-QCR-1800-1010 | Structural Outfitting
| ITR-203 |  |  |  |  | PMA-BHP-QC-TST-0147/ PR18015-900-QCR-1800-1011 | Structual Shop Release Note
[6 empty] | PMA-BHP-QC-TST-0148/ PR18015-900-QCR-1800-1012 | Structural Bolting Final Inspection
[6 empty] | PMA-BHP-QC-TST-0149/ PR18015-900-QCR-1800-1013 | Structural Members
Structural | ITR-301 | ITR-ME-016 | STRUCTURAL STEEL ERECTION | ITR-ME-016 | STRUCTURAL STEEL ERECTION | PMA-BHP-QC-TST-0151/ PR18015-900-QCR-2300-1001 | Shop Painting and Blasting per Batch
| ITR-302 | ITR-ME-017 | STRUCTURAL STEEL VERTICALITY | ITR-ME-006 | STRUCTURAL STEEL VERTICALITY | PMA-BHP-QC-TST-0159/ PR18015-900-QCR-2300-1010 | AQIS Compliance Check List
| ITR-303 | ITR-ME-018 | EXPOXY GROUTING | ITR-ME-013 | EXPOXY GROUTING | PMA-BHP-QC-TST-0153/ PR18015-900-QCR-2300-1004 | Field Painting
| ITR-304 | ITR-ME-019 | CEMENTITIOUS GROUTING |  |  | PMA-BHP-QC-TST-0171/ PR18015-900-QCR-2300-1015 | Protective Coatings and Painting – Final Inspection
|  | ITR-ME-015 | BOLT TENSIONING RECORD | ITR-ME-015 | BOLT TENSIONING RECORD
|  |  |  | ITR-ME-014 | GROUTING CHECKSHEET
Mechanical | ITR-401 | ITR-ME-010 | MECHANICAL PRE-COMMISSIONING | ITR-ME-011 | MECHANICAL PRE-COMMISSIONING
| ITR-402 | ITR-ME-011 | SLIDING VANE PUMPS | ITR-ME-009 | SLIDING VANE PUMPS
| ITR-403 | ITR-ME-012 | CENTRIFUGAL PUMPS | ITR-ME-010 | CENTRIFUGAL PUMPS
| ITR-404 | ITR-ME-013 | DRIVE COUPLING ALIGNMENT | ITR-ME-017 | DRIVE COUPLING ALIGNMENT
| ITR-405 | ITR-ME-014 | PACKAGED EQUIPMENT PRE-COMMISSIONING | ITR-ME-012 | PACKAGED EQUIPMENT PRE-COMMISSIONING
ITR-406
Piping | ITR-501 | ITR-ME-001 | PIPING INSTALLATION | ITR-ME-001 | PIPING INSTALLATION
| ITR-502 | ITR-ME-002 | UNDERGROUND PIPING INSTALLATION | ITR-ME-002 | UNDERGROUND PIPING INSTALLATION
| ITR-503 | ITR-ME-003 | SPOOL CLEANLINESS AND DRYING SUMMARY | ITR-ME-003 | SPOOL CLEANLINESS AND DRYING SUMMARY
| ITR-504 | ITR-ME-004 | FLANGE CLOSURE REGISTER | ITR-ME-004 | FLANGE CLOSURE REGISTER
| ITR-505 | ITR-ME-005 | HYDROTEST REPORT SUMMARY | ITR-ME-005 | HYDROTEST REPORT SUMMARY
| ITR-506 | ITR-ME-006 | WELD REPAIR AUTHORISATION | ITR-ME-007 | WELD REPAIR AUTHORISATION
| ITR-507 | ITR-ME-007 | WELD TRACEABILITY SHEET | ITR-ME-008 | WELD TRACEABILITY SHEET
| ITR-508 | ITR-ME-008 | FLOW RATE CHECKSHEET | ITR-ME-018 | FLOW RATE CHECKSHEET
| ITR-509 | ITR-ME-009 | PATCH TEST REPORT | ITR-ME-019 | PATCH TEST REPORT
|  |  |  | ITR-ME-020 | PIPING FLUSHING TEST SHEET
|  |  |  | ITR-ME-021 | HYDROTEST REPORT
|  |  |  | ITR-ME-022 | PIPING DRYING TEST SHEET

## ITP-102
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Earthworks
Final Release by: | Client Approval |  | DISCLIPLINE | Earthworks
INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Preceding Tasks
1.1 | Site Handover | Handover Letter | Sign and Approve Handover Letter | TO BE CONSTRUCTED | H |  | H
1.2 | Specification Sign Off | 100-SP-CI-0007 100-SP-CI-0004 100-SP-CI-0002 | Approval of Specification Documents | TO BE CONSTRUCTED | H |  | H
1.3 | Bulk Compaction Testing Sign Off | Bulk Compaction Test Results | Approval of Bulk Compaction Test Results | TO BE CONSTRUCTED | H |  | H
4 | Material Compliance and Certification
4.1 | Crushed Rock | 100-SP-CI-0007 | Comply with Specifications and Standards |  | W |  | M
4.2 | Fill Materials | 100-SP-CI-0007 AS 1289 AS 1152 AS 1141 | Comply with Specifications and Standards |  | W |  | M
5 | Excavation
5.1 | Approved Drawings | AFC Drawings | Approval of Drawings | 02704-ITR-001 | H |  | M
5.2 | Approved Specification | 100-SP-CI-0007 | Approval of Specification | 02704-ITR-001 | H |  | H
6 | Backfill
6.1 | Compaction Thickness Layers | 100-SP-CI-0007 | Comply with Specifications | 02704-ITR-001 | W |  | M
7 | Compaction
7.1 | Compaction Thickness Layers | 100-SP-CI-0007 | Comply with Specifications | 02704-ITR-001 | W |  | M
8 | Tolerance of Earthworks
8.1 | Surface Levels | 100-SP-CI-0007 Section 15 |  | 02704-ITR-001 | W |  | M
8.2 | Grade Condition | 100-SP-CI-0007 Section 15 |  | 02704-ITR-001 | W |  | M
8.3 | Finishing Tolerances | 100-SP-CI-0007 Section 15 |  | 02704-ITR-001 | W |  | H
9 | Earthworks Testing
9.1 | Instrument Calibration | 100-SP-CI-0007 Section 16.3 |  | Calibration Certificate | W |  | W
9.2 | Acceptance Testing | 100-SP-CI-0007 Section 13.3 100-SP-CI-0007 Section 16.4 |  | Compaction Certificate | W |  | M
9.3 | Frequency of Testing | 100-SP-CI-0007 Section 13.4 100-SP-CI-0007 Appendix 1 & 2 AS3798-2007 Table 8.1 |  | NATA Certificate | W |  | M
Legend: W = Witness; R = Review; H = Hold; I = In-House; SU = Surveillance; S = Sub-Supplier; FM = Foreman; ENG = Engineer; SV = Surveyor; SC = Subcontractor; PT = Project Team; WS = Witness first time then random

## ITP-204
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Concrete
Final Release by: | Client Approval |  | DISCLIPLINE | Civil
INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Planning
1.1 | Quality Management Plan |  | Submitted & Approved |  | H |  | H
1.2 | Construction Drawings |  | AFC Drawings |  | H |  | H
1.3 | Safe Work Instructions |  | Submitted & Approved |  | R |  | R
1.4 | Approval of Concrete Mix Design | AFC Drawings | AS-1379 | NATA Test Results | R |  | H
2 | Formwork Installation
2.1 | Confirm formwork is secured to correct lines and levels | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 |  |  | M
2.2 | Survey formwork to ensure within tolerance | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
2.3 | Inspect formwork to ensure compliance to design | 100-SP-CI-0003 | Formwork Drawings | ITR 203, ITR-204 | W |  | M
3 | Reinforcment Installation
3.1 | Reinforcement is processed, bent to specifications | 100-SP-CI-0003 | AS-4671 | ISO 9001 | R |  | R
3.2 | Reinforcement is bundled, tagged and stored to specifications | 100-SP-CI-0003 | AS-4671 | Delivery Schedules | W,R |  | M
3.1 | Ensure all materials are clean, cut and bent to schedules | 100-SP-CI-0003 | AFC Drawings AS-4671 | ITR 203, ITR-204 | M |  | M
3.2 | Confirm all reinforcement is in place and secured | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
3.3 | Check cover is in compliance to specifications and drawings | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
3.4 | Ensure all supports, chairs, blocks are in place | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
3.5 | Verify splicing is as per drawings and specifications | 100-SP-CI-0003 | AFC Drawings AS-3600 | ITR 203, ITR-204 | W |  | M
3.6 | Check reinforcement is sufficiently fixed | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
4 | Embedments
4.1 | Embedments are to specifications, HD bolts, cast in angles, plates and ferrules | 100-SP-CI-0003 | AFC Drawings AS-4100 | , Galvanising reportsVendor's ITP Mill Certificates WPQ's, WP's, Material reports, ITR 203, ITR-204 | W |  | W
4.2 | Lifting anchors and brace points | Approved engineered shop drawings | AS-3850 AS-3600 | Manufacturer's report Lifting, engineered design, ITR-204 | W |  | W
4.3 | Placement of embedment items are to specifications and drawings | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
4.4 | Final visual inspection of all embedments final pre pour survey of embedment items | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | W |  | M
4.5 | placement to ensure within tolerance | 100-SP-CI-0003 | Survey Report | ITR 203, ITR-204 | W |  | R
5 | Concrete Placement
5.1 | Signed off Concrete Pre Pour ITR's | 100-SP-CI-0003 | AFC Drawings | ITR 203, ITR-204 | H |  | H
5.2 | Correct Mix Code Delivered | 100-SP-CI-0003, Trial Mix | AFC Drawings | Batch Docket | W |  | M
5.3 | Concrete Testing - Temperture, Slump Strength | 100-SP-CI-0003 | AS-1012 AS-1379 | Field Testing Sheet, NATA Test Results | W |  | R
5.4 | Concrete placement | 100-SP-CI-0003 | AS-3600 AFC Drawings | ITR 203, ITR-204 | W |  | M
5.5 | Construction Joints | 100-SP-CI-0003 | AS-3600 AFC Drawings | ITR-206, ITR 203, ITR-204 | W |  | M
5.6 | Compaction | 100-SP-CI-0003 |  |  | W |  | M
5.7 | Curing | 100-SP-CI-0003 | AS-3799 | ITR 203, ITR-204, Manufacturer's TDS | W |  | M
5.8 | Inspect concrete surfaces after formwork removal | 100-SP-CI-0003 | AS3600 | ITR-206 | W |  | R
5.9 | Concrete Repairs | 100-SP-CI-0003 | Approved Concrete Repair Methodology | ITR-206 | W |  | W
6 | Inspection
6.1 | Survey and issue as built of completed structure | 100-SP-CI-0003 | AFC Drawings | Survey Reports | H |  | R
7 | Close Out Documentation
7.1 | Compile and submit all signed QA documentation | 100-SP-CI-0003 |  | MDR | R,S |  | R

## ITP-304
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Steel Fabrication
Final Release by: | Client Approval |  | DISCLIPLINE | Structural
INSPECTION AND VERIFICATION
[5 empty] | Metros |  | EPCM |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | WELD QUALIFICATIONS & PROCEDURES
1.01 | Approval of qualified WPS documents.; | 505PC0001-00000-SP-ST-0001_REV0 |  | Approved WPQR's and WPSs |  |  | AP
1.02 | Approval of welder qualification documents.; | 505PC0001-00000-SP-ST-0001_REV0 |  | Approved WPQR's and WPSs |  |  | AP
1.03 | Approval of WPS & welder qualification register.; | 505PC0001-00000-SP-ST-0001_REV0 |  | Approved WPQR's and WPSs |  |  | AP
1.04 | Issue MDR list of contents; | 505PC0001-00000-SP-ST-0001_REV0 |  | All Relevant Q.A Documentation MDR Index |  |  | RE
2 | ISSUE MATERIALS
2.01 | Receive and 100% visual check all relevant material mill certificates; | 505PC0001-00000-SP-ST-0001_REV0 |  | Material Certificates & Delivery Docket | RE |  | R
2.02 | Material check: quantities, damage, size/type.; | 505PC0001-00000-SP-ST-0001_REV0 |  | Material Certificates & Delivery Docket | R
2.03 | Have all material laid down in metro delivery area; |  |  | Material Certificates & Delivery Docket
3 | PREPARATION OF MATERIALS
3.01 | Check material type & grade; | 505PC0001-00000-SP-ST-0001_REV0 |  | Work Order IFC Drawings | V
3.02 | Cut & mark materials; | 505PC0001-00000-SP-ST-0001_REV0 |  | IFC Shop Drawings | D
4 | FABRICATION
4.01 | Wps to be issued to welders & is to be fully accessible at all times; |  |  | Approved WPQR's and WPSs | V |  | S
4.02 | Check that material is correct; |  |  | Work Order IFC Drawings | V
4.03 | Prepare & assemble; |  |  | IFC Shop Drawings | R
4.04 | Check fit up for visual & dimensional acceptance; |  |  | IFC Shop Drawings | D
4.05 | Check welder qualifications; |  |  | Approved WPQR's, WPSs & Register | V
4.06 | Check welds & root pass using approved wps & welders; |  |  | Approved WPQR's & WPS's | RE
4.07 | Check final welds (welds inspected after minimum 24 hrs); |  |  | Drawings; Weld Inspection Reports; Approved WPQR's & WPS's | D
4.08 | Make sure holes are de burred; |  |  | Approved WPQR's & WPS's | R
4.09 | Check for sharp edges & insure edges are cleaned; |  |  | Approved WPQR's & WPS's | R
4.1 | Check for any distortions to steel; |  |  | Approved WPQR's & WPS's & IFC Shop Drawings | D
4.11 | Insure all steel has correct mark numbers; |  |  | IFC Shop Drawings | V
4.12 | An accurate final dimensional & visual check is crucial; | 505PC0001-00000-SP-ST-0001_REV0 |  | IFC Shop Drawings | AP |  | AC
4.13 | Insert if reqd breather vent holes 6mm for galv; | 505PC0001-00000-SP-ST-0001_REV0 |  | IFC Shop Drawings | V
5 | NDT
5.01 | 100% Visual Weld Inspection | 505PC0001-00000-SP-ST-0001_REV0 |  | Metro Lintels Checkers Signature On As Built Shop Drawings | V
5.02 | Fillet welds - 10% MT; Butt welds - 10% UT; Butt welded splices - 100% UT; All carried out by 3rd party (NATA accredited lab) as per AS 1554; | 505PC0001-00000-SP-ST-0001_REV0 |  | Nata Report Signed | AC |  | RE
5.03 | All Lifting Lugs 100% UT & MT - UT Base Metal & Welds, MT Finished Weld; | 505PC0001-00000-SP-ST-0001_REV0 |  | Nata Report Signed | AC |  | RE
6 | FINAL INSPECTION
6.01 | Check off delivery docket before being sent for treatment; |  |  | Delivery Docket To Treatment Yard Checked & Signed | V |  | H
7 | SURFACE TREATMENT
7.01 | Refer to ITP-999 Surface Treatment;
8 | DELIVERY
8.01 | Load steel on trailer - complete delivery docket supplied to transport stating all relevant information for all members. loading as per site requirements for unloading of steel of transport. (pre slung or ewp access); | 505PC0001-00000-SP-ST-0001_REV0 |  | Delivery Docket From Paint Yard Checked & Signed | AP |  | H
Legend: W = Witness; R = Review; H = Hold; I = In-House; SU = Surveillance; S = Sub-Supplier; FM = Foreman; ENG = Engineer; SV = Surveyor; SC = Subcontractor; PT = Project Team; WS = Witness first time then random

## ITP-306
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Structural Steel Surface Treatment
Final Release by: | Client Approval |  | DISCLIPLINE | Structural
INSPECTION AND VERIFICATION
[5 empty] | Metros |  | EPCM |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | PRELIMINARIES
1.1 | ITP Development |  | Appendix D - CL2.2 | Quality Management Plan, Approved ITP | H
2 | Surface Treatment
2.1 | Coating Systems & Products in accordance with drawings specifications |  | Coating system complies with design and specs | Signed ITP | H
2.2 | Limits of areas/surfaces to be coated indicated & surrounding areas protected to prevent damage |  | Appropriate protection provided to areas not to be painted | Signed ITP | W
2.3 | Surface prepared in accordance with specifications & supplier data whip blast Gal steel to achieve blast profile 25um |  | Surface prepared IAW Specification & Supplier data | Inspection report | WS
2.4 | Coating materials prepared & mixed adequately in accordance with manufactures recommendations |  | Materials prepared IAW Suppliers data | Inspection report | W
2.5 | Surface Coatings applied in accordance with specified protection systems G3 SP118 50um interguard 251, apply finish coat of interfine 629 75um |  | Surface Coatings applied IAW specified protection systems and schedule | Inspection report | R
2.6 | Coat finish acceptable: Surface smooth, free from holes and defects, thickness complies with specified protection systems |  | Contain thickness IAW specifications and supplier data Tolerance of 0 to 20% Minimum DFT | Coating thickness report from subcontractor | W
2.7 | Items protected, stored, handled & Transported correctly |  | Items protected,stored, hauled & transported IAW specifications | Signed ITP | R
2.8 | Lot Conforms |  | Appendix F - CL2, 4.3 | Signed ITP | SU
3 | Documentation | ITP
3.1 | Verify all documentations are signed |  | - | - | R
3.2 | File all relevant documentation and reports in the MDR |  | Appendix D - CL2.3 | - | R
Legend: W = Witness; R = Review; H = Hold; I = In-House; SU = Surveillance; S = Sub-Supplier; FM = Foreman; ENG = Engineer; SV = Surveyor; SC = Subcontractor; PT = Project Team; WS = Witness first time then random

## ITP-504
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Piping Installation
Final Release by: | Client Approval |  | DISCLIPLINE | Piping
INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Approvals & Mobilisation
1.1 | Complete and Submit Weld Procedure Specifications & Qualifications | WPS & WPQ Reports | ASME IX; B31.3 | Approved WPS’s
1.2 | Qualify Welders prior to mobilisation and submit Qualifications | Welder Qualification Reports | ASME IX; B31.3 | Approved Welder Qualifications
2 | Materials
2.1 | Monitor Incoming Materials (New) | Purchase Order; AFC Drawings; Delivery Dockets | Purchase Order; AFC Drawings | Signed Delivery Dockets; Material Certificates, Inspection Certificates
2.2 | Material Traceability | AFC Drawings & Client Specifications | Materials Specifications | Traceability Records for Piping Works
2.3 | Received fabricated piping. | AFC Drawings & Client Specifications | ASME B31.3; AFC Drawings | ITR’s and Traceability Records
3 | On Site Installation
3.1 | Mark materials / spools / for cutting & weld preparation. Dimensional check fabricated spools and existing infrastructure. | AFC Drawings; EO01-SP-PI-003 | AFC Drawings; EO01-SP-PI-003 | AFC Drawings; Cutting List;
3.2 | Prepare cut materials / spools for Installation. | AFC Drawings; EO01-SP-PI-003 | AFC Drawings; EO01-SP-PI-003 | AFC Drawings
3.3 | Consumables Control | Purchase Order; EO01-SP-PI-003 | ASME B31.3; EO01-SP-PI-003 | Consumables Certificates
3.4 | Assemble material components as per drawing. | AFC Drawings; EO01-SP-PI-003 | AFC Drawings; EO01-SP-PI-003 | AFC Drawings
3.5 | Dimensional & fit up inspection prior to welding | AFC Drawings; EO01-SP-PI-003 | ASME IX; Approved WPS | AFC Drawings
3.6 | Welding of assembled components | Client Specifications; EO01-SP-PI-003 | ASME IX; Approved WPS
3.7 | Complete Hydrotesting of all required lines | Client SOW; EO01-SP-PI-003; Hydrotest procedures | Client Specifications; EO01-SP-PI-003 | Approved WPS’s; Traceability Records; Signed ITR’s & Hydrotest Reports- NATA
3.8 | Complete PWHT on required spooling | Client Specifications; EO01-SP-PI-003 | ASME IX; Approved WPS | Approved WPS’s; Traceability Records
3.9 | Complete final visual inspection and completion of all required ITR’s in a work pack format with all required data as identified. | Client Specifications; EO01-SP-PI-003 | ASME B31.3; Work Pack ITR’s | AFC Drawings; Signed off documents contained in ITR’s
4 | Inspection & Testing
4.1 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc | Client SOW; EO01-SP-PI-003; NDT Procedure | ASME B31.3 NFS; AFC Drawings | AFC Drawings; Material release note; NDT / NATA reports
4.2 | NDT on Complete spools Prior to outages and tie-in welds | Client SOW; EO01-SP-PI-003; NDT Procedure | ASME B31.3 NFS; AFC Drawings | AFC Drawings; Include in ITR’s; NDT / NATA reports
5 | On-Site Surface Treatment
5.1 | Prime after receiving all relevant permits and risk assessment completed. | Client SOW; EO01-SP-ME-006 | ASME B31.3 NFS; AFC Drawings | Surface Treatment Reports,; Contractor’s ITP
5.2 | Complete applicable surface treatment | Client SOW; EO01-SP-ME-006 | ASME B31.3 NFS; AFC Drawings; ITRS | Surface Treatment Reports,; Contractor’s ITP
6 | Clean up & demobilise
6.1 | Pack up materials and equipment | Despatch Dockets | Client SOW | Despatch Notes, Signed off ITP
6.2 | Clean-up site | Client Requirements | Client SOW | Practical Completion Certificate
7 | Documentation (MDR)
7.1 | MDR (Compiled Progressively) per compressor station | Contract Document | Clients Requirements | Approved MDR for; Offsite Works

## ITP-701
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Electrical and Instrimentation Main Site Setup
Final Release by: | Client Approval |  | DISCLIPLINE | Electrical
INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Site Preparation, Planning and Inspection | 01707‐SWI‐HS‐093 Site Preparation, Planning and Inspection | N/A | N/A
2 | Generator and Main Distribution Board Laydown | 00000-SWI-HS-003_0 Vehicle & Truck Loading Unloading and Load Restraints | Visual Checks As Per ITR | 00000-ITR-EL-011_1 Distribution Board Installation | R
|  | 00000-SWI-HS-016_0 Franna Crane | Performance Resistance/Continuity Tests (3.1), verify results do not vary by >10%
|  | 00000-PRO-HS-004_0 Lifting Operations | Performance Resistance/Continuity Tests (3.2), verify results do not vary by ≥ 100MΩ | 00000-ITR-EL-046_0 Synchronous Generator Motor Installation
|  | 00000-SWI-HS-025_0 Manual Handling | Perform Other Equipment Insulation Resistance tests (3.3) and verify results are ≥ 100MΩ
3 | Installation of Electrical Earthing | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per IPR | 01707‐ITR‐EL‐015 Electrical Earthing | W,R
|  | 01707‐PRO‐EL‐005 Inspection Test Record Procedure | All Earthing Conductors properly installed , protected and continuously tested (overall value to be less than 0.5Ω)
00000-SPC-EL-001_A Electrical Installation Specification 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure
2 | Installation of Cable Ladders and Trays | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per ITR | 01707‐ITR‐EL‐033 Cable Tray ‐ Ladder | R
01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐SWI‐HS‐091 Installation of Cable Tray and Cable Ladder 01707‐PRO‐EL‐004A Electrical ITR Matrix Procedure
00000-PRO-HS-004_0 Lifting Operations
3 | Installation of Below Ground Conduits | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per ITR | 01707‐ITR‐EL‐036 Underground Cable Installation | W,R
|  | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐SWI‐HS‐094 Trenching, Excavating, Pot Holing 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure |  | 00000-ITR-EL-050_0 Underground Conduit Installation
4 | Installation of Aboveground Rigid Discontinuous Conduit | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per ITR | 01707‐ITR‐EL‐034 Above Ground Conduit | R
01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure
5 | Installation of Cables and Fibre Optic Cables | 00000-SPC-EL-001_A Electrical Installation Specification | Earthing Conductors and Armour must be less than 0.5Ω | 01707‐ITR‐EL‐001 On Drum Testing for Cables 01707‐ITR‐EL‐002 Cable Installation 01707‐ITR‐EL‐036 Underground Cable Installation | W,R
|  | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐SWI‐HS‐092 Installation of Cables 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Insulation Check must be greater than 10MΩ
8 | Testing and Termination Cables | 00000-SPC-EL-001_A Electrical Installation Specification | Earthing Conductors and Armour must be less than 0.5Ω | 01707‐ITR‐EL‐003 Cable Test 01707‐ITR‐EL‐004 Cable Termination | R
|  | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Insulation Check must be greater than 10MΩ
9 | Installation of Local Control Stations | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Visual Checks As Per ITR | 01707‐ITR‐EL‐030 Local Control | R
10 | Installation of Lighting and lighting Poles | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Visual Checks As Per ITR | 01707‐ITR‐EL‐029 Lighting | R
11 | Installation of Control Panel | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Visual Checks As Per ITR | 01707‐ITR‐EL‐023 Control Panel | R
12 | Installation of Instruments | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Visual Checks As Per ITR | 01707‐ITR‐IN‐001 Instrument Installation 01707‐ITR‐IN‐003 Equipment Pre‐ Installation Verification | R
13 | Installation of Instrument Tubing | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Visual Checks As Per ITR | 01707‐ITR‐IN‐006 Instrument Tubing Installation | R
14 | Instrument Loop Checks | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Visual Checks As Per ITR | 01707‐ITR‐IN‐007 Instrument Loop Check | R
15 | Notice Of Energisation | 0000-PRO-CN-001 Notice of Energisation Procedure | Visual Checks As Per ITR | 00000-ITR-EL-045_A Energisation Report | R
00000-PRO-EL-001_0 Isolation Procedure
Legend: W = Witness; R = Review; H = Hold; I = In-House; SU = Surveillance; S = Sub-Supplier; FM = Foreman; ENG = Engineer; SV = Surveyor; SC = Subcontractor; PT = Project Team; WS = Witness first time then random

## ITP-702
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  | SCOPE OF ITP: | Electrical and Instrimentation Site Setup
Final Release by: | Client Approval |  | DISCLIPLINE | Electrical
INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR CRITERIA | ACCEPTANCE CRITERIA | VERYIFING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | Site Preparation, Planning and Inspection | 01707‐SWI‐HS‐093 Site Preparation, Planning and Inspection | N/A | N/A
2 | Generator and Main Distribution Board Laydown | 00000-SWI-HS-003_0 Vehicle & Truck Loading Unloading and Load Restraints | Visual Checks As Per ITR | 00000-ITR-EL-011_1 Distribution Board Installation | R
|  | 00000-SWI-HS-016_0 Franna Crane | Performance Resistance/Continuity Tests (3.1), verify results do not vary by >10%
|  | 00000-PRO-HS-004_0 Lifting Operations | Performance Resistance/Continuity Tests (3.2), verify results do not vary by ≥ 100MΩ | 00000-ITR-EL-046_0 Synchronous Generator Motor Installation
|  | 00000-SWI-HS-025_0 Manual Handling | Perform Other Equipment Insulation Resistance tests (3.3) and verify results are ≥ 100MΩ
3 | Installation of Electrical Earthing | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per IPR | 01707‐ITR‐EL‐015 Electrical Earthing | W,R
|  | 01707‐PRO‐EL‐005 Inspection Test Record Procedure | All Earthing Conductors properly installed , protected and continuously tested (overall value to be less than 0.5Ω)
00000-SPC-EL-001_A Electrical Installation Specification 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure
4 | Installation of Cable Ladders and Trays | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per ITR | 01707‐ITR‐EL‐033 Cable Tray ‐ Ladder | R
01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐SWI‐HS‐091 Installation of Cable Tray and Cable Ladder 01707‐PRO‐EL‐004A Electrical ITR Matrix Procedure
00000-PRO-HS-004_0 Lifting Operations
5 | Installation of Aboveground Rigid Discontinuous Conduit | 00000-SPC-EL-001_A Electrical Installation Specification | Visual Checks As Per ITR | 01707‐ITR‐EL‐034 Above Ground Conduit | R
01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure
6 | Testing and Termination Cables | 00000-SPC-EL-001_A Electrical Installation Specification | Earthing Conductors and Armour must be less than 0.5Ω | 01707‐ITR‐EL‐003 Cable Test 01707‐ITR‐EL‐004 Cable Termination | R
|  | 01707‐PRO‐EL‐005 Inspection Test Record Procedure 01707‐PRO‐EL‐004_A Electrical ITR Matrix Procedure 01707‐PRO‐EL‐002_A Electrical Testing and Reporting Procedure 01707‐PRO‐EL‐007 Calibration and Equipment Procedure | Insulation Check must be greater than 10MΩ
7 | Notice Of Energisation | 0000-PRO-CN-001 Notice of Energisation Procedure | Visual Checks As Per ITR | 00000-ITR-EL-045_A Energisation Report | R
00000-PRO-EL-001_0 Isolation Procedure

## Piping & Mechanical Matrix
Inspection and Test Record Matrix
|  | Piping | [8 empty] | Mechanical | [5 empty] | Structural/Civil
SMP ITR MATRIX | ITR NUMBER | ITR-ME-001 | ITR-ME-002 | ITR-ME-003 | ITR-ME-004 | ITR-ME-005 | ITR-ME-006 | ITR-ME-007 | ITR-ME-008 | ITR-ME-009 | ITR-ME-010 | ITR-ME-011 | ITR-ME-012 | ITR-ME-013 | ITR-ME-014 | ITR-ME-015 | ITR-ME-016 | ITR-ME-017 | ITR-ME-018 | ITR-ME-019 | ITR-ME-020 | ITR-ME-022 | ITR-ME-023 | ITR-ME-024 | ITR-ME-025 | ITR-ME-026 | ITR-ME-027 | ITR-ME-028 | ITR-ME-029 | ITR-ME-030
ITEM | ITR DESCRIPTION | PIPING INSTALLATION | UNDERGROUND PIPING INSTALLATION | SPOOL CLEANLINESS AND DRYING SUMMARY | FLANGE CLOSURE REGISTER | HYDROTEST REPORT SUMMARY | WELD REPAIR AUTHORISATION | WELD TRACEABILITY SHEET | FLOW RATE CHECKSHEET | PATCH TEST REPORT | MECHANICAL PRE-COMMISSIONING | SLIDING VANE PUMPS | CENTRIFUGAL PUMPS | DRIVE COUPLING ALIGNMENT | PACKAGED EQUIPMENT PRE-COMMISSIONING | BOLT TENSIONING RECORD | STRUCTURAL STEEL ERECTION | STRUCTURAL STEEL VERTICALITY | EXPOXY GROUTING | CEMENTITIOUS GROUTING
Pipe Fabrication |  | P
Piping Protective Coatings
Piping (in test pack & reinstatement pack) |  | P |  | P | P | P | P | P | P
Piping - underground |  |  | P
Golden Weld | [7 empty] | P
Joint Integrity | [7 empty] | P
Seal welds | [7 empty] | P
Vessels | [10 empty] | P |  |  |  | P | P |  |  | P
Columns | [10 empty] | P |  |  |  | P | P |  |  | P
Towers | [10 empty] | P |  |  |  | P | P |  |  | P
Pumps (Centrifugal) | [10 empty] | P |  | P | P | P | P |  |  | P
Pumps (Sliding Vane) | [10 empty] | P | P |  | P | P | P |  |  | P
Compressors | [10 empty] | P |  |  |  | P | P |  |  | P
Fans | [10 empty] | P |  |  |  | P | P |  |  | P
Heat Exchangers | [10 empty] | P |  |  |  | P | P |  |  | P
Tanks | [10 empty] | P |  |  |  | P | P |  |  |  | P
Gas turbines | [10 empty] | P |  |  |  | P | P |  |  | P
Generators | [10 empty] | P |  |  |  | P | P |  |  | P
Platforms | [15 empty] | P | P | P |  | P
Skids | [10 empty] | P |  |  |  |  | P | P | P |  | P
Walkways | [15 empty] | P | P | P |  | P

## Structural & Civil Works
Doc. No : PMA-TE1-QC-MTX-0001 Rev : 1 Page : 13 of 13
|  | Civil | [13 empty] | Structural
Civil Works ITR MATRIX | DESCRIPTION | Excavation and Backfill | Reinforcement Checklist | Formwork Checklist | Concrete Supply Checklist | Concrete Foundation Preparation and Pour | Concrete Record | Precast Units | Building and Civil Works | Survey/ Acceptance for Concrete Structures | Roadworks | Civil Works - Storm Water Drainage | Grouting Pre Pour Inspection and Application | Fences and Gates | Paving | Grouting Pre Pour Inspection and Application | Site Installation and Assembly | High Strength Bolting | Equipment Erection Survey Report | Structural Alignment of Beams | Structural Alignment of Columns | Steel Structures Final inspection | Structural Steel - Workshop Fabrication | Structural Outfitting | Structual Shop Release Note | Structural Bolting Final Inspection | Structural Members | Shop Painting and Blasting per Batch | AQIS Compliance Check List | Field Painting | Protective Coatings and Painting – Final Inspection
ITEM | ITR TYPE | PMA-BHP-QC-TST-0125/ PR18015-900-QCR-1700-1001 | PMA-BHP-QC-TST-0126/ PR18015-900-QCR-1700-1002 | PMA-BHP-QC-TST-0127/ PR18015-900-QCR-1700-1003 | PMA-BHP-QC-TST-0128/ PR18015-900-QCR-1700-1004 | PMA-BHP-QC-TST-0129/ PR18015-900-QCR-1700-1005 | PMA-BHP-QC-TST-0130/ PR18015-900-QCR-1700-1006 | PMA-BHP-QC-TST-0131/ PR18015-900-QCR-1700-1007 | PMA-BHP-QC-TST-0132/ PR18015-900-QCR-1700-1008 | PMA-BHP-QC-TST-0133/ PR18015-900-QCR-1700-1009 | PMA-BHP-QC-TST-0134/ PR18015-900-QCR-1700-1010 | PMA-BHP-QC-TST-0135/ PR18015-900-QCR-1700-1011 | PMA-BHP-QC-TST-0136/ PR18015-900-QCR-1700-1012 | PMA-BHP-QC-TST-0137/ PR18015-900-QCR-1700-1013 | PMA-BHP-QC-TST-0138/ PR18015-900-QCR-1700-1014 | PMA-BHP-QC-TST-0136/ PR18015-900-QCR-1700-1012 | PMA-BHP-QC-TST-0139/ PR18015-900-QCR-1800-1001 | PMA-BHP-QC-TST-0140/ PR18015-900-QCR-1800-1002 | PMA-BHP-QC-TST-0141/ PR18015-900-QCR-1800-1003 | PMA-BHP-QC-TST-0142/ PR18015-900-QCR-1800-1004 | PMA-BHP-QC-TST-0143/ PR18015-900-QCR-1800-1005 | PMA-BHP-QC-TST-0144/ PR18015-900-QCR-1800-1006 | PMA-BHP-QC-TST-0145/ PR18015-900-QCR-1800-1007 | PMA-BHP-QC-TST-0146/ PR18015-900-QCR-1800-1010 | PMA-BHP-QC-TST-0147/ PR18015-900-QCR-1800-1011 | PMA-BHP-QC-TST-0148/ PR18015-900-QCR-1800-1012 | PMA-BHP-QC-TST-0149/ PR18015-900-QCR-1800-1013 | PMA-BHP-QC-TST-0151/ PR18015-900-QCR-2300-1001 | PMA-BHP-QC-TST-0159/ PR18015-900-QCR-2300-1010 | PMA-BHP-QC-TST-0153/ PR18015-900-QCR-2300-1004 | PMA-BHP-QC-TST-0171/ PR18015-900-QCR-2300-1015
Roads, Yards & Paving | [10 empty] | ü |  |  |  | ü
Earthworks |  | ü
Bases & Pedestals |  | ü | ü | ü |  | ü |  |  |  | ü
Fences & Gates | [13 empty] | ü
Stormwater & Oilywater |  | ü | ü | [8 empty] | ü
Structural Steel (Construction) | [9 empty] | ü | [5 empty] | ü | ü | ü |  | ü | ü | ü |  |  |  | ü | ü |  |  | ü | ü
Structural Steel (Fabrication) | [9 empty] | ü | [7 empty] | ü |  | ü | ü |  | ü |  | ü |  |  | ü | ü
Buildings | [9 empty] | ü | [13 empty] | ü | [6 empty] | ü

## ITP-304 draft
inspection & test plan
ITP No: |  | TITLE: |  | EQUIPMENT: Steel Fabrication
Prepared By: |  |  | Date: | CUSTOMER REFERENCE:
Reviewed By: |  |  | Date: | ACTIVITY VERIFICATION
|  |  |  | METROS |  | EPCM |  | 3RD PARTY |  | REMARKS
ITEM No | ACTIVITY DESCRIPTION | ACCEPTANCE CRITERIA | DELIVERABLE DOCUMENTATION | REQ'D | SIGN | REQ'D | SIGN | REQ'D | SIGN
1 | WELD QUALIFICATIONS & PROCEDURES
1.01 | Approval of qualified WPS documents.; | 505PC0001-00000-SP-ST-0001_REV0 | Approved WPQR's and WPSs |  |  | AP
1.02 | Approval of welder qualification documents.; | 505PC0001-00000-SP-ST-0001_REV0 | Approved WPQR's and WPSs |  |  | AP
1.03 | Approval of WPS & welder qualification register.; | 505PC0001-00000-SP-ST-0001_REV0 | Approved WPQR's and WPSs |  |  | AP
1.04 | Issue MDR list of contents; | 505PC0001-00000-SP-ST-0001_REV0 | All Relevant Q.A Documentation MDR Index |  |  | RE
2 | ISSUE MATERIALS
2.01 | Receive and 100% visual check all relevant material mill certificates; | 505PC0001-00000-SP-ST-0001_REV0 | Material Certificates & Delivery Docket | RE |  | R
2.02 | Material check: quantities, damage, size/type.; | 505PC0001-00000-SP-ST-0001_REV0 | Material Certificates & Delivery Docket | R
2.03 | Have all material laid down in metro delivery area; |  | Material Certificates & Delivery Docket
3 | PREPARATION OF MATERIALS
3.01 | Check material type & grade; | 505PC0001-00000-SP-ST-0001_REV0 | Work Order IFC Drawings | V
3.02 | Cut & mark materials; | 505PC0001-00000-SP-ST-0001_REV0 | IFC Shop Drawings | D
4 | FABRICATION
4.01 | Wps to be issued to welders & is to be fully accessible at all times; |  | Approved WPQR's and WPSs | V |  | S
4.02 | Check that material is correct; |  | Work Order IFC Drawings | V
4.03 | Prepare & assemble; |  | IFC Shop Drawings | R
4.04 | Check fit up for visual & dimensional acceptance; |  | IFC Shop Drawings | D
4.05 | Check welder qualifications; |  | Approved WPQR's, WPSs & Register | V
4.06 | Check welds & root pass using approved wps & welders; |  | Approved WPQR's & WPS's | RE
4.07 | Check final welds (welds inspected after minimum 24 hrs); |  | Drawings; Weld Inspection Reports; Approved WPQR's & WPS's | D
4.08 | Make sure holes are de burred; |  | Approved WPQR's & WPS's | R
4.09 | Check for sharp edges & insure edges are cleaned; |  | Approved WPQR's & WPS's | R
4.1 | Check for any distortions to steel; |  | Approved WPQR's & WPS's & IFC Shop Drawings | D
4.11 | Insure all steel has correct mark numbers; |  | IFC Shop Drawings | V
4.12 | An accurate final dimensional & visual check is crucial; | 505PC0001-00000-SP-ST-0001_REV0 | IFC Shop Drawings | AP |  | AC
4.13 | Insert if reqd breather vent holes 6mm for galv; | 505PC0001-00000-SP-ST-0001_REV0 | IFC Shop Drawings | V
5 | NDT
5.01 | 100% Visual Weld Inspection | 505PC0001-00000-SP-ST-0001_REV0 | Metro Lintels Checkers Signature On As Built Shop Drawings | V
5.02 | Fillet welds - 10% MT; Butt welds - 10% UT; Butt welded splices - 100% UT; All carried out by 3rd party (NATA accredited lab) as per AS 1554; | 505PC0001-00000-SP-ST-0001_REV0 | Nata Report Signed | AC |  | RE |  | V
5.03 | All Lifting Lugs 100% UT & MT - UT Base Metal & Welds, MT Finished Weld; | 505PC0001-00000-SP-ST-0001_REV0 | Nata Report Signed | AC |  | RE |  | V
6 | FINAL INSPECTION
6.01 | Check off delivery docket before being sent for treatment; |  | Delivery Docket To Treatment Yard Checked & Signed | V |  | H
7 | SURFACE TREATMENT
7.01 | Refer to ITP-999 Surface Treatment;
8 | DELIVERY
8.01 | Load steel on trailer - complete delivery docket supplied to transport stating all relevant information for all members. loading as per site requirements for unloading of steel of transport. (pre slung or ewp access); | 505PC0001-00000-SP-ST-0001_REV0 | Delivery Docket From Paint Yard Checked & Signed | AP |  | H
KEY: |  | COMMENTS: | [5 empty] | REV | DATE | REVISION DETAIL
AP = APPROVAL | S = SURVEILLANCE | 1. Separate ITP’s are required from Sub-Contractors, if used.
V = VERIFY | R = RANDOM | 2. All deliverable documentation including this completed ITP shall be included in the Manufacturers Data Report.
RE = REVIEW | D = DIMENSIONAL CHECK | 3. This ITP shall be presented to the Customers’ representative for signature at each mandatory Hold point, as a minimum.
H = HOLD | AC = ACCEPTANCE | 4. A separate ITP shall be produced for each separate work package.
W = WITNESS

## ITP-305 draft
inspection & test plan
ITP No: |  | TITLE: |  | EQUIPMENT: Steel Fabrication
Prepared By: |  |  | Date: | CUSTOMER REFERENCE:
Reviewed By: |  |  | Date: | ACTIVITY VERIFICATION
|  |  |  | METROS |  | EPCM |  | 3RD PARTY |  | REMARKS
ITEM No | ACTIVITY DESCRIPTION | ACCEPTANCE CRITERIA | DELIVERABLE DOCUMENTATION | REQ'D | SIGN | REQ'D | SIGN | REQ'D | SIGN
1 | WELD QUALIFICATIONS & PROCEDURES
1.01 | Approval of qualified WPS documents.; | 505PC0001-00000-SP-ST-0001_REV0 | Approved WPQR's and WPSs |  |  | AP
1.02 | Approval of welder qualification documents.; | 505PC0001-00000-SP-ST-0001_REV0 | Approved WPQR's and WPSs |  |  | AP
1.03 | Approval of WPS & welder qualification register.; | 505PC0001-00000-SP-ST-0001_REV0 | Approved WPQR's and WPSs |  |  | AP
1.04 | Issue MDR list of contents; | 505PC0001-00000-SP-ST-0001_REV0 | All Relevant Q.A Documentation MDR Index |  |  | RE
2 | ISSUE MATERIALS
2.01 | Receive and 100% visual check all relevant material mill certificates; | 505PC0001-00000-SP-ST-0001_REV0 | Material Certificates & Delivery Docket | RE |  | R
2.02 | Material check: quantities, damage, size/type.; | 505PC0001-00000-SP-ST-0001_REV0 | Material Certificates & Delivery Docket | R
2.03 | Have all material laid down in metro delivery area; |  | Material Certificates & Delivery Docket
3 | PREPARATION OF MATERIALS
3.01 | Check material type & grade; | 505PC0001-00000-SP-ST-0001_REV0 | Work Order IFC Drawings | V
3.02 | Cut & mark materials; | 505PC0001-00000-SP-ST-0001_REV0 | IFC Shop Drawings | D
4 | FABRICATION
4.01 | Wps to be issued to welders & is to be fully accessible at all times; |  | Approved WPQR's and WPSs | V |  | S
4.02 | Check that material is correct; |  | Work Order IFC Drawings | V
4.03 | Prepare & assemble; |  | IFC Shop Drawings | R
4.04 | Check fit up for visual & dimensional acceptance; |  | IFC Shop Drawings | D
4.05 | Check welder qualifications; |  | Approved WPQR's, WPSs & Register | V
4.06 | Check welds & root pass using approved wps & welders; |  | Approved WPQR's & WPS's | RE
4.07 | Check final welds (welds inspected after minimum 24 hrs); |  | Drawings; Weld Inspection Reports; Approved WPQR's & WPS's | D
4.08 | Make sure holes are de burred; |  | Approved WPQR's & WPS's | R
4.09 | Check for sharp edges & insure edges are cleaned; |  | Approved WPQR's & WPS's | R
4.1 | Check for any distortions to steel; |  | Approved WPQR's & WPS's & IFC Shop Drawings | D
4.11 | Insure all steel has correct mark numbers; |  | IFC Shop Drawings | V
4.12 | An accurate final dimensional & visual check is crucial; | 505PC0001-00000-SP-ST-0001_REV0 | IFC Shop Drawings | AP |  | AC
4.13 | Insert if reqd breather vent holes 6mm for galv; | 505PC0001-00000-SP-ST-0001_REV0 | IFC Shop Drawings | V
5 | NDT
5.01 | 100% Visual Weld Inspection | 505PC0001-00000-SP-ST-0001_REV0 | Metro Lintels Checkers Signature On As Built Shop Drawings | V
5.02 | Fillet welds - 10% MT; Butt welds - 10% UT; Butt welded splices - 100% UT; All carried out by 3rd party (NATA accredited lab) as per AS 1554; | 505PC0001-00000-SP-ST-0001_REV0 | Nata Report Signed | AC |  | RE |  | V
5.03 | All Lifting Lugs 100% UT & MT - UT Base Metal & Welds, MT Finished Weld; | 505PC0001-00000-SP-ST-0001_REV0 | Nata Report Signed | AC |  | RE |  | V
6 | FINAL INSPECTION
6.01 | Check off delivery docket before being sent for treatment; |  | Delivery Docket To Treatment Yard Checked & Signed | V |  | H
7 | SURFACE TREATMENT
7.01 | Refer to ITP-999 Surface Treatment;
8 | DELIVERY
8.01 | Load steel on trailer - complete delivery docket supplied to transport stating all relevant information for all members. loading as per site requirements for unloading of steel of transport. (pre slung or ewp access); | 505PC0001-00000-SP-ST-0001_REV0 | Delivery Docket From Paint Yard Checked & Signed | AP |  | H
KEY: |  | COMMENTS: | [5 empty] | REV | DATE | REVISION DETAIL
AP = APPROVAL | S = SURVEILLANCE | 1. Separate ITP’s are required from Sub-Contractors, if used.
V = VERIFY | R = RANDOM | 2. All deliverable documentation including this completed ITP shall be included in the Manufacturers Data Report.
RE = REVIEW | D = DIMENSIONAL CHECK | 3. This ITP shall be presented to the Customers’ representative for signature at each mandatory Hold point, as a minimum.
H = HOLD | AC = ACCEPTANCE | 4. A separate ITP shall be produced for each separate work package.
W = WITNESS

## ITP-306 (draft)
CLIENT: | Fortescue Metals Group
PROJECT: | Ammonium Nitrate Storage Facility- Solomon |  |  |  |  | DOCUMENT:
REV:
CLIENT REFERENCE No:
Prepared By: | Henry Smith |  |  |  |  | SCOPE OF ITP: | Structural Steel Surface Treatment
Final Release by: | Client Approval |  |  |  |  | DISCLIPLINE | Structural
INSPECTION AND VERIFICATION
[8 empty] | Primero |  | Client |  | 3rd Party Inspection
ITEM NO: | INSPECTION AND TEST ACTIVITY | RESPONSIBLE PERSON | INSPECTION TEST / METHOD | FREQUENCY | CONTROLLING PROCEDURE, INSTRUCTION OR SPECIFICATION | ACCPTANCE CRITERIA | VERIFYING DOCUMENT | ACT. | SIG. | ACT. | SIG. | ACT. | SIG.
1 | PRELIMINARIES
1.1 | ITP Development | PT, ENG,SC | Documentation Review | Prior to Commencement |  | Appendix D - CL2.2 | Quality Management Plan, Approved ITP | H
2 | Surface Treatment
2.1 | Coating Systems & Products in accordance with drawings specifications | PT, ENG, SC | Review | Prior to Commencement |  | Coating system complies with design and specs | Signed ITP | H
2.2 | Limits of areas/surfaces to be coated indicated & surrounding areas protected to prevent damage | SC | Review | Prior to Commencement |  | Appropriate protection provided to areas not to be painted | Signed ITP | W
2.3 | Surface prepared in accordance with specifications & supplier data whip blast Gal steel to achieve blast profile 25um | SC | Visual, Review | Each Lot |  | Surface prepared IAW Specification & Supplier data | Inspection report | WS
2.4 | Coating materials prepared & mixed adequately in accordance with manufactures recommendations | SC | Visual | Each Lot |  | Materials prepared IAW Suppliers data | Inspection report | W
2.5 | Surface Coatings applied in accordance with specified protection systems G3 SP118 50um interguard 251, apply finish coat of interfine 629 75um | SC | Visual | Each Lot |  | Surface Coatings applied IAW specified protection systems and schedule | Inspection report | R
2.6 | Coat finish acceptable: Surface smooth, free from holes and defects, thickness complies with specified protection systems | SC | Visual | Each Lot |  | Contain thickness IAW specifications and supplier data Tolerance of 0 to 20% Minimum DFT | Coating thickness report from subcontractor | W
2.7 | Items protected, stored, handled & Transported correctly | SC | Visual | Each Lot |  | Items protected,stored, hauled & transported IAW specifications | Signed ITP | R
2.8 | Lot Conforms | PT, SC | Review | Every despatch |  | Appendix F - CL2, 4.3 | Signed ITP | SU
3 | Documentation
3.1 | Verify all documentations are signed | PT, SC | Review | At Completion | ITP | - | - | R
3.2 | File all relevant documentation and reports in the MDR | PT, SC | Review | At Completion |  | Appendix D - CL2.3 | - | R
Legend: W = Witness; R = Review; H = Hold; I = In-House; SU = Surveillance; S = Sub-Supplier; FM = Foreman; ENG = Engineer; SV = Surveyor; SC = Subcontractor; PT = Project Team; WS = Witness first time then random
INSPECTION AND TEST PLAN 02704-ITP-CI-???