## Sheet1
ITP Discipline |  | Piping Supply, Fabrication and Assembly WIP |  | Project Area | Yamarna Gas Pipeline & Stations
Project Title |  | Design and Supply of Yamarna Gas Skids |  | Revision | B
Primero Document No. |  | 06702-ITP-PP-001 |  | Date | 2017-10-20
Client |  | APA Group |  | Prepared | R. O’Callaghan
Client Document No. |  | YGP-020-ITP-QM-0001 |  | Approved | B. Zlnay
H = HOLD POINT |  | V = VISUAL INSPECTION | R = REVIEW & COMMENT | D = DIMENSIONAL INSPECTION |  | WR = WITNESS @ RANDOM
W = WITNESS POINT |  | M = MONITOR ON A RANDOM BASIS | A = APPROVE | S = SUBMIT DOCUMENT TO CLIENT
REF | INSPECTION AND TEST ACTIVITY | APPLICABLE DOCUMENT OR PROCEDURE ETC. | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | INSPECTION AND VERIFICATION
[5 empty] | Primero |  | Client |  | 3RD Party Inspection
[5 empty] | Activity | Signature | Activity | Signature | Activity | Signature
1 | SPECIFICATIONS
1.1 | Review Scope of Work | YGP-SOW-A-0001 | Not Applicable | Contract Document | R |  | R
1.2 | Review Design | Packaged Equipment Specification, YGP-SP-A-0002 | YGP-SOW-A-0001 | Design Approval, VDS | R |  | R
1.3 | Review Drawings | AFC Drawings | Not Applicable | AFC Drawings | S |  | R
2 | APPROVALS
2.1 | Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures | ITP, NDE Procedure, Pressure Testing Procedure, Coating Procedure | 530-SP-P-0002 ASME B31.3 530-SP-M-9602 | Approved ITP, NDE Procedure, Pressure Testing Procedure, Coating Procedure | S, H |  | A, H
2.2 | Submit Weld Procedure Specifications & Qualifications | WPS & WPQ Records | ASME IX 530-SP-P-0002 YGP-SP-A-0002 | Approved WPSs | S, H |  | A, H, W
2.3 | Submit Welder Qualifications | Welder Qualification Reports & Register | ASME IX 530-SP-P-0002 YGP-SP-A-0002 | Approved Welder Qualifications | S, H |  | A, H, W
3 | MATERIALS
3.1 | Monitor Incoming Materials | Design drawings; 530-SP-S-0004, Materials Management Procedure YGP-020-PL-QM-0001 | 530-SP-P-0002 | Signed Delivery Dockets; Material Certificates, Inspection Certificates | R, W |  | W
3.2 | Material Traceability | 530-SP-P-0002 Individual markings to correspond to certificates; Management Procedure YGP-020-PL-QM-0001 | Materials Specifications EN10204 3.1 | Traceability Records for Piping Works YGP-020-SCH-A-003 Material Certificates Register | R |  | M
4 | MATERIALS PREPARATION
4.1 | Mark materials for cutting & weld preparation. Dimensional check. | Piping Isometrics drawings | 530-SP-P-0002 | YGP-020-SCH-A-003 | R |  | M
4.2 | Prepare controlled/cut materials for fabrication | Material Control procedure | 530-SP-P-0002, ASME B31.3 | YGP-020-SCH-A-003 | R |  | M
4.3 | Consumables Control | Consumable Control Procedure | 530-SP-P-0002, ASME B31.3, Manufacturers Recommendations | Consumables Register Consumables Certificates | R |  | M
5 | FABRICATION
5.1 | Assemble material components as per drawing. | Project Execution Plan - YGP-020-PL-A-0001, ASME PCC-1, General Arrangement Drawings | 530-SP-P-0002, ASME B31.3 | 06702-ITP-PP-001 | R |  | M
5.2 | Dimensional check & fit up inspection prior to welding | Dimensional checks, YGP-020-PL-QM-0001 | 530-SP-P-0002, ASME B31.3 Isometric & fabrication detail drawings | 06702-ITP-PP-001 | R |  | M
5.3 | Welding of assembled components | Approved WPS, WPQR and Welder Qualifications | 530-SP-P-0002, ASME B31.3 | Weld/Welder Traceability documentation YGP-020-SCH-A-003 | R |  | M
5.4 | Ongoing visual weld inspection of all welded components. | Project Execution Plan - YGP-020-PL-A-0001, ASME PCC-1, General Arrangement Drawings, WPS | 530-SP-P-0002, ASME B31.3 | YGP-020-SCH-A-003 | R |  | M
6 | INSPECTION & TESTING
6.1 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc. | Fabrication/dimensional control procedure YGP-020-PL-QM-0001 | 530-SP-P-0002, ASME B31.3, 530-SP-P-0002– isometric & fabrication detail drawings | As Builts, Visual Inspection Records | R |  | WR
6.2 | NDE in accordance with approved drawings, specifications | Subcontractor NDE Procedures (Document # TBA) | 530-SP-P-0002, ASME B31.3 | Certified NATA reports; YGP-020-SCH-A-003, Weld Maps, NDE Traceability Records | R |  | WR,R
6.3 | Weld repairs | Repair Procedure | 530-SP-P-0002, ASME B31.3 | Certified NATA reports Repair Records | H |  | H
6.4 | Hydrotest | Subcontractor Pressure Testing Procedures (Document # TBA) | 530-SP-P-0002, ASME B31.3 | Certified NATA reports 06702-ITR-PP-105 | H |  | H
6.5 | Draining and Drying | Subcontractor Pressure Testing Procedures (Document # TBA) | 530-SP-P-0002, ASME B31.3 | Certified NATA reports 06702-ITR-PP-105 | H |  | H
7 | SURFACE TREATMENT
7.1 | Complete applicable surface treatment | Coating Subcontractor Procedure, Coating Subcontractor ITP | Surface Treatment and Finishes, 530-SP-M-9602 | Surface Treatment Records | R |  | WR, R
8 | ASSEMBLY / INSTALLATION ONTO SKIDS
8.1 | Assemble material components as per drawing | ASME PCC-1 | AFC Drawings | 06702-ITR-PP-101 | M |  | M
8.2 | Dimensional & fit up inspection prior to tensioning | ASME PCC-1 | ASME B31.3 AFC Drawings 530-SP-P-0002 YGP-SP-A-0002 | 06702-ITR-PP-101 | M |  | M
8.3 | Complete flange fit ups in accordance with ITR and standards – flange and valve faces to be clean, free of damage and imperfections | Flange Management Procedure Bolt Torque Procedure ASME PCC-1 | ASME B31.3, ASME B16.5 Table 3 530-DWG-M-0100 530-SP-P-0002 YGP-SP-A-0002 | 06702-ITR-PP-101 Flange management tags Bolt Torque Records Work Pack ITR’s | H |  | WR
8.4 | Complete final visual inspection and completion of all required ITR’s in a work pack format with all required data as identified. | Project Execution Plan - YGP-020-PL-A-0001 ASME PCC-1 General Arrangement Drawings | ASME B31.3 530-SP-P-0002 YGP-SP-A-0002 | As-built Drawings, 06702-ITR-PP-101 Punch Lists Work Pack ITR’s | H |  | WR
9 | DESPATCH
9.1 | Internal Cleanliness | Mechanical Equipment and Pipework Cleaning - 530-SP-M-9610 | 530-SP-P-0002 YGP-SP-A-0002 | 06702-ITR-PP-101 | W, H |  | W, H
9.2 | Preparation & packaging for transport & load out to site, ensuring packaging will limit chance of condensation and flash corrosion of pipe internals by using sealed end caps | Shipping, Packing , Preservation and Storage Procedure - YGP-020-PR-A-0005 Photos | 530-SP-P-0002 Preservation for Packing, Shipping and Handling - 530-SP-A-0002 YGP-SP-A-0002 | Delivery Documentation Inspection release form, Load Hazard Analysis, Shipping Details and Packing List, photos | W, H |  | W, H
9.3 | Final Inspection | YGP-SOW-A-0001, 530-SP-P-0002, YGP-SP-A-0002 | 530-SP-P-0002, YGP-SP-A-0002 | Inspection Release Certificate | W, H |  | W, H
9.4 | Delivery to Site | Inspection release – review & acceptance | 530-SP-P-0002, YGP-SP-A-0002 | 06702-ITP-PP-001, Delivery Documentation | W, H |  | W, H
10 | VERIFICATION
10.1 | Punchlisting | AFC Drawings, YGP-SOW-A-0001 | AFC Drawings, YGP-SOW-A-0001 | Completed Client Punchlist | H |  | H

## Sheet2
3 | On Site Installation
3.1 | Mark materials / spools / for cutting & weld preparation. Dimensional check fabricated spools and existing infrastructure. | AFC Drawings, Project Piping Specification 1155-EM-SPE-008 | AFC Drawings | AFC Drawings, Cutting List | R | R
3.2 | Prepare cut materials / spools for Installation. | AFC Drawings | AFC Drawings | AFC Drawings | R | R
3.3 | Consumables Control | Purchase Order | ASME B31.3 | Consumables Certificates | M | R
3.4 | Assemble material components as per drawing. | AFC Drawings | AFC Drawings | AFC Drawings, 03404-ITR-ME-001 | M | R
3.5 | Dimensional & fit up inspection prior to welding | AFC Drawings | ASME IX, Approved WPS | AFC Drawings, 03404-ITR-ME-001 | M | R
3.6 | Welding of assembled components | Client Specifications | ASME IX, Approved WPS | Approved WPSs, Traceability Records | M | R
3.8 | Complete flange fit ups in accordance with ITR and standards – flange and valve faces to be clean, free of damage and imperfections | Client Specifications | ASME B31.3, ASME B16.5 Table 3, Work Pack ITR’s | AFC Drawings, 03404-ITR-ME-001 | H | R
3.9 | Complete final visual inspection and completion of all required ITR’s in a work pack format with all required data as identified. | Client Specifications | ASME B31.3, Work Pack ITR’s | AFC Drawings, 03404-ITR-ME-001 | H | R
4 | Inspection & Testing
4.1 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc | Client SOW, NDT Procedure | ASME B31.3, AFC Drawings | AFC Drawings, Material release note, NDT / NATA reports | H | R
4.2 | NDT on Complete spools Prior to outages and tie-in welds | Client SOW, NDT Procedure, % as defined on isometrics | ASME B31.3, AFC Drawings, ITRs | AFC Drawings, Include in ITRs, NDT / NATA reports | H | R
4.3 | Complete Hydrotesting of all required lines | Client SOW, Hydrotest procedures | Client Specifications | Signed 03404-ITR-ME-005 & Hydrotest Reports- NATA | H | R
5 | On-Site Surface Treatment
5.1 | Prime after receiving all relevant permits and risk assessment completed. | Client SOW | Client SOW | Surface Treatment Reports and 03404-ITR-ME-001 | M | R
5.2 | Complete applicable surface treatment | Client SOW | Client SOW | Surface Treatment Reports and 03404-ITR-ME-001 | S | R