## Register
INSPECTION AND TEST PLAN (ITP) REGISTER
|  | CLIENT : | Rio Tinto
|  | PROJECT : | Yandi Sustaining Project |  |  | Submitted
|  | PROJECT No : | 1707 |  |  | Completed Not Submitted
|  | SITE : | Yandicoogina Mine |  |  | To be revised
|  | LAST UPDATED : | 2014-08-08
ITR No. | Title |  |  | Originator | Date Issued | Date Completed
ITP-001 | OFF SITE PIPING SUPPLY AND FABRICATION |  |  | Brian Zlnay | 2014-08-01 | XX/XX/XXXX
ITP-002 | OFF SITE STRUCTURAL SUPPLY AND FABRICATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-003 | DIESEL TANKS YTK605 & YTK606 AND WALKWAYS INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-004 | OILY WATER SEPARATOR INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-005 | DIESEL PUMPS SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-008 | DIESEL FILTERS SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-009 | DIESEL REFUELLING ARM SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-010 | PIPING INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-011 | STRUCTURAL STEELWORK AND PIPE SUPPORTS INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-013 | ELECTRICAL AND INSTRUMENTATION INSTALLATION JSW - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-014 | ELECTRICAL AND INSTRUMENTATION INSTALLATION JC - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX

## ITP-001
ITP Number: |  | 01707-ITP-QA-001 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0003 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Subcontractor | PIVS Engineering | Equipment Number: | Piping Package |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | PIPING SUPPLY AND FABRICATION – OFF SITE
Works Locations: |  | Fabrication Workshop
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | W |  | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 & Data Sheets | Not applicable | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, VDDI | W |  | W |  | SV
2 |  | APPROVALS
2.1 | 2014-06-01 | Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures | I | ITP, NDE procedures, Pressure testing procedures | Not applicable | Approved ITP’s NDE procedures, Pressure testing procedures | W, H |  | W, H
2.2 | 2014-06-01 | Submit Weld Procedure Specifications & Qualifications | I | WPS & WPQ Reports | ASME IX; AS1554; | Approved WPSs | H |  | H |  | R
2.3 | 2014-06-01 | Submit Welder Qualifications | I | Welder Qualification Reports & register | ASME IX; AS1554; | Approved Welder Qualifications | H |  | H |  | R
3 |  | MATERIALS
3.1 | 2014-06-15 | Monitor Incoming Materials (New) And Client supply | I | Client MTO; YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022; 01707-LST-ME-001 | YSP-0000-SPE-M-001 (Section 8,9) | Signed Delivery Dockets; Material Certificates, Inspection Certificates | SV, W |  | SV, W |  | SV
3.2 | 2014-06-15 | Material Traceability | I | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records for Piping Works | SV |  | SV |  | R
4 |  | MATERIALS PREPARATION
4.1 | 2014-06-17 | Mark materials for cutting & weld preparation. Dimensional check. | S | Piping Isometrics & structural detail drawings | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, 01707-ITR-ME-008 | SV |  | SV |  | R
4.2 | 2014-06-17 | Prepare controlled/cut materials for fabrication | S | Material Control procedure, 01707-PLN-PM-002 | YSP-0000-SPE-M-001 (Section 2), AS4041 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, 01707-ITR-ME-008 | SV |  | SV |  | SV
4.3 | 2014-06-17 | Consumables Control | S | Consumable Control Procedure, 01707-PLN-PM-002 | YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1553 | Manufacturers Recommendations | SV |  | SV |  | SV
5 |  | FABRICATION
5.1 | 2014-06-17 | Assemble material components as per drawing. | S | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 | YSP-0000-SPE-M-001 (Section 2), AS4041 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 | SV |  | SV |  | SV
5.2 | 2014-06-17 | Dimensional check & fit up inspection prior to welding | S | Dimensional check procedure, 01707-PLN-PM-002 | YSP-0000-SPE-M-001 (Section 2), AS4041 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 – isometric & fabrication detail drawings | SV |  | SV |  | SV
5.3 | 2014-06-17 | Welding of assembled components | S | Weld/Welder Traceability documentation | YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554 | Approved WPS’s; 01707-ITR-ME-008 | SV |  | SV |  | SV
5.4 | 2014-06-17 | Ongoing visual weld inspection of all welded components. | S | Client Specifications, WPS | YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554 | 01707-ITR-ME-008 | SV |  | SV |  | SV
6 |  | INSPECTION & TESTING
6.1 | 2014-07-15 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc | I | Dimensional check procedure, 01707-QA-PRO-003 | YSP-0000-SPE-M-001 (Section 2), AS4041 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 – isometric & fabrication detail drawings | SV |  | SV |  | SV
6.2 | 2014-07-15 | NDE in accordance with approved drawings, specifications | S | NDE Procedures; YSP-0000-SPE-M-001 (Section 2) | YSP-0000-SPE-M-001 (Section 2), AS4041 | Certified NATA reports; 01707-ITR-ME-007 | SV |  | SV |  | R
6.3 | 2014-07-15 | Weld repairs | S | NDE Procedures; YSP-0000-SPE-M-001 (Section 2) | YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554 | Certified NATA reports; 01707-ITR-ME-006 | H |  | H |  | R/SV
6.4 | 2014-07-15 | Hydrotest | S | YSP-0000-SPE-M-001 (Section 2) | YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554 | Certified NATA reports; 01707-ITR-ME-005 | H |  | H |  | W
6.5 | 2014-07-15 | Pickling/Chemical Treatment | S | YSP-0000-SPE-M-001 (Section 2.5) | YSP-0000-SPE-M-001 (Section 2.5), ASME IX, AS1627 Part 5 | Subcontractor repair; 01707-ITR-ME-003 | H |  | H |  | W
7 |  | OFFSITE SURFACE TREATMENT
7.1 | 2014-07-20 | Grit blast and prime | S | SS-P118_2 (Section 7) | SS-P118_2 (Section 7) | Surface Treatment Records | SV |  | SV |  | R/SV
7.2 | 2014-07-20 | Complete applicable surface treatment | S | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | SV |  | SV |  | R/SV
8 |  | ASSEMBLY & VERIFICATION
8.1 | 2014-07-25 | Piping completion and verification | S | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-M-001 (Section 8,9) | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 & Specifications | SV |  | SV |  | SV
8.2 | 2014-07-25 | Punch listing completed | S | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-M-001 (Section 8,9) | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, Punchlist & Specifications | H |  | H |  | SV
9 |  | DESPATCH
9.1 | 2014-08-01 | Review completed ITP | I | 01707-ITP-QA-001 | Not applicable | Approved ITP | SV, R |  | SV, R |  | SV
9.2 | 2014-08-01 | Preparation & packaging for transport & load out to site, ensuring packaging will limit chance of condensation and flash corrosion of pipe internals by using sealed end caps | I | Inspection release form, Load Hazard Analysis, Shipping Details and Packing List, Material Equipment Movement Form, photos | Inspection release form, Load Hazard Analysis, Shipping Details and Packing List, Material Equipment Movement Form | Delivery Documentation | W, H |  | W, H |  | R
9.3 | 2014-08-01 | Final Inspection | I | Inspection release form | Primero Form | Delivery Documentation | W, H |  | W, H |  | R
9.4 | 2014-08-01 | Delivery to Site | I | Inspection release – review & acceptance | Primero Form | Inspection Acceptance form | W, H |  | W, H |  | R
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-002
ITP Number: |  | 01707-ITP-QA-002 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0004 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | C | Subcontractor | PIVS Engineering | Equipment Number: | Structural Package |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | STRUCTURAL SUPPLY AND FABRICATION - OFF SITE
Works Locations: |  | Fabrication Workshop
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | W |  | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 & Data Sheets | Not applicable | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002, VDDI | W |  | W |  | SV
2 |  | APPROVALS
2.1 | 2014-07-01 | Submit Project Documentation, ITP, NDE procedures | I | ITP, NDE procedures, Pressure testing procedures | Not applicable | Approved ITP’s NDE procedures, Pressure testing procedures | W, H |  | W, H |  | H
2.2 | 2014-07-01 | Submit Weld Procedure Specifications & Qualifications | I | WPS & WPQ Reports | ASME IX; AS1554; | Approved WPSs | H |  | H |  | H
2.3 | 2014-07-01 | Submit Welder Qualifications | I | Welder Qualification Reports & register | ASME IX; AS1554; | Approved Welder Qualifications | H |  | H |  | H
3 |  | MATERIALS
3.1 | 2014-07-15 | Monitor Incoming Materials (New) And Client supply | I | Client MTO; YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002; 01707-LST-ME-001 | YSP-0000-SPE-S-002 (Section 4) | Signed Delivery Dockets; Material Certificates, Inspection Certificates | SV, W |  | SV, W |  | SV
3.2 | 2014-07-15 | Material Traceability | I | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | W |  | SV |  | R
4 |  | MATERIALS PREPARATION
4.1 | 2014-07-17 | Mark materials for cutting & weld preparation. Dimensional check. | S | Structural detail drawings | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002, 01707-ITR-ME-008 | W |  | SV |  | R
4.2 | 2014-07-17 | Prepare controlled/cut materials for fabrication | S | Material Control procedure, 01707-PLN-PM-002 | YSP-0000-SPE-S-002 (Section 4), AS4100 | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002, 01707-ITR-ME-008 | W |  | SV |  | SV
4.3 | 2014-07-17 | Consumables Control | S | Consumable Control Procedure, 01707-PLN-PM-002 | YSP-0000-SPE-S-002 (Section 4), ASME IX, AS1553 | Manufacturers Recommendations | W |  | SV |  | SV
5 |  | FABRICATION
5.1 | 2014-07-17 | Assemble material components as per drawing. | S | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 | YSP-0000-SPE-S-002 (Section 6), AS4100 | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 | W |  | SV |  | SV
5.2 | 2014-07-17 | Dimensional check & fit up inspection prior to welding | S | Dimensional check procedure, 01707-PLN-PM-002 | YSP-0000-SPE-S-002 (Section 6), AS4100 | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 – fabrication detail drawings | H |  | W |  | SV
5.3 | 2014-07-17 | Welding of assembled components | S | Weld/Welder Traceability documentation | YSP-0000-SPE-S-002 (Section 6), ASME IX, AS1554 | Approved WPS’s; 01707-ITR-ME-008 | W |  | SV |  | SV
5.4 | 2014-07-17 | Ongoing visual weld inspection of all welded components. | S | Client Specifications, WPS | YSP-0000-SPE-S-002 (Section 6), ASME IX, AS1554 | 01707-ITR-ME-008 | W |  | SV |  | SV
6 |  | INSPECTION & TESTING
6.1 | 2014-08-15 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc | I | Dimensional check procedure, 01707-QA-PRO-003 | YSP-0000-SPE-S-002 (Section 8), AS4100 | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 – fabrication detail drawings | W |  | SV |  | SV
6.2 | 2014-08-15 | NDE of components or lifting lugs (100%) in accordance with drawings/specifications | S | NDE Procedures; YSP-0000-SPE-S-002 (Section 8) | YSP-0000-SPE-S-002 (Section 8), AS4100 | Certified NATA reports; 01707-ITR-ME-007 | H |  | W |  | R
6.3 | 2014-08-15 | Weld repairs | S | NDE Procedures; YSP-0000-SPE-S-002 (Section 8) | YSP-0000-SPE-S-002 (Section 8), ASME IX, AS1554 | Certified NATA reports; 01707-ITR-ME-007 | H |  | H |  | R/SV
7 |  | OFFSITE SURFACE TREATMENT
7.1 | 2014-08-20 | Grit blast and prime | S | SS-P118_2 (Section 7) | SS-P118_2 (Section 7) | Surface Treatment Records | SV |  | SV |  | R/SV
7.2 | 2014-08-20 | Complete applicable surface treatment | S | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | SV |  | SV |  | R/SV
8 |  | ASSEMBLY & VERIFICATION
8.1 | 2014-08-25 | Structural completion and verification | S | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002 & Specifications | SV |  | SV |  | SV
8.2 | 2014-08-25 | Punch listing completed | S | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VS-00001, 00002, 00003, YA-2829-VM-00001, YA-2829-VS-00001, 00002, Punchlist & Specifications | H |  | H |  | R
9 |  | DESPATCH
9.1 | 2014-09-05 | Review completed ITP | I | 01707-ITP-QA-002 | Not applicable | Approved ITP | SV, R |  | SV, R |  | R
9.2 | 2014-09-05 | Preparation & packaging for transport & load out to site, ensuring packaging will limit chance of corrosion | I | Inspection release form, Load Hazard Analysis, Shipping Details and Packing List, Material Equipment Movement Form, photos | Inspection release form, Load Hazard Analysis, Shipping Details and Packing List, Material Equipment Movement Form | Delivery Documentation | W, H |  | W, H |  | R
9.3 | 2014-09-05 | Final Inspection | I | Inspection release form | Primero Form | Delivery Documentation | W, H |  | W, H |  | R
9.4 | 2014-09-05 | Delivery to Site | I | Inspection release – review & acceptance | Primero Form | Inspection Acceptance form | W, H |  | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-003
ITP Number: |  | 01707-ITP-QA-003 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0005 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: | YTK605 & YTK606 |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | DIESEL TANKS YTK605 & YTK606 AND WALKWAYS INSTALLATION
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VM-00003, 00004 & Data Sheets | Not applicable | YA-2963-VM-00003, 00004, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP, NDE procedures | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
2.2 | 2014-08-01 | Submit Weld Procedure Specifications & Qualifications | I | WPS & WPQ Reports | ASME IX; AS1554; | Approved WPSs | NA | NA | H |  | R
2.3 | 2014-08-01 | Submit Welder Qualifications | I | Welder Qualification Reports & register | ASME IX; AS1554; | Approved Welder Qualifications | NA | NA | H |  | R
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply, confirming preservation intact after shipping | I | MTO; YA-2963-VM-00003, 00004; 01707-LST-ME-001 | YSP-0000-SPE-S-002 (Section 4) | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VM-00003, 00004, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | NA | NA | SV |  | R
4 |  | TANKS INSTALLATION | I
4.1 | 2014-09-20 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | SV
4.2 | 2014-09-20 | All footings shall be scabbled prior to install of equipment and structures | I | Vendor IOM, Scope of Work, | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | H
4.3 | 2014-09-20 | Install chemical anchors as per manufacturers directions | I | Vendor IOM, Scope of Work, Chemical Anchor IOM | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Chemical Anchor IOM, Survey Report (where required) | NA | NA | W |  | SV
4.4 | 2014-09-20 | Check that levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of each tank. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.5 | 2014-09-20 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required) | I | Construction Methodology (Schedule M of the Contract) | Australian Standards and Regulations | Certification, Approved Lift Study Report where required | NA | NA | H |  | W
4.6 | 2014-09-20 | Land each tank and confirm tie in points are within tolerance |  | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.7 | 2014-09-23 | Erect walkway columns and beams. | I | Construction Methodology (Schedule M of the Contract) | AS 4100, YSP-0000-S-002, Approved Drawings | 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.8 | 2014-09-23 | Structure Installed and checked (Location/ Elevation/ level) Snug tighten Primary connections throughout the structure | I | Construction Methodology (Schedule M of the Contract) | AS 4100, YSP-0000-S-002 | Visual Inspection or Survey Report (where required) | NA | NA | H |  | W
4.9 | 2014-09-23 | Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-006, Survey Report | NA | NA | W |  | SV
4.10 | 2014-09-23 | Tension all secondary steel bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.11 | 2014-09-26 | Grating and handrails to be installed as required to ensure safe work practice and access. | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-006, Survey Report | NA | NA | W |  | SV
4.12 | 2014-09-26 | Confirm piping tie-ins are complete and grout tanks and walkways. Check and verify grouting is acceptable | I | YSP-2963-SOW-M-001, Manufacturers directions | AFC Drawings, Vendor IOM | Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 | NA | NA | H |  | W
4.13 | 2014-09-26 | Tension all hold down bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.14 | 2014-09-26 | Ensure no stress on nozzles from piping connection | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-011 | NA | NA | R |  | SV
4.15 | 2014-09-26 | Ensure preservation and maintenance as per manufacturer recommendation | I | YSP-2963-SOW-M-001 | Vendor IOM | Vendor IOM | NA | NA | W |  | R
5 |  | ASSEMBLY & VERIFICATION
5.1 | 2014-09-30 | Structural and mechanical completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00003, 00004 & Specifications | NA | NA | W |  | R
5.2 | 2014-09-30 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00003, 00004, Punchlist & Specifications | NA | NA | H |  | SV
6 |  | INSPECTION & TESTING
6.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-003 | Not applicable | Approved ITP | NA | NA | R |  | R
6.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-003 | Not applicable | Approved ITP | NA | NA | W, H |  | R
6.3 | 2014-11-01 | Commission equipment in accordance with Commissioning Test Procedure | I | Commissioning Test Procedure, Manufacturers IOM | Commissioning Test Procedure, Manufacturers IOM | Approved CTP | NA | NA | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-004
ITP Number: |  | 01707-ITP-QA-004 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0006 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: | YOS605 |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | OILY WATER SEPARATOR YOS605 INSTALLATION
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VP-00001, YA-2963-VC-00002 & Data Sheets | Not applicable | YA-2963-VP-00001, YA-2963-VC-00002, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply, confirming preservation intact after shipping | I | MTO; YA-2963-VP-00001, YA-2963-VC-00002; 01707-LST-ME-001 | YSP-2963-SOW-M-001, SS-M101 | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VP-00001, YA-2963-VC-00002, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | NA | NA | SV |  | R
4 |  | OILY WATER SEPARATOR SKIDS INSTALLATION | I
4.1 | 2014-09-20 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | SV
4.2 | 2014-09-20 | All footings shall be scabbled prior to install of equipment and structures | I | Vendor IOM, Scope of Work, | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | H
4.3 | 2014-09-20 | Install chemical anchors as per manufacturers directions | I | Vendor IOM, Scope of Work, Chemical Anchor IOM | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Chemical Anchor IOM, Survey Report (where required) | NA | NA | W |  | SV
4.4 | 2014-09-20 | Check that levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of each skid. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.5 | 2014-09-20 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required) | I | Construction Methodology (Schedule M of the Contract) | Australian Standards and Regulations | Certification, Approved Lift Study Report where required | NA | NA | H |  | W
4.6 | 2014-09-20 | Land each skid and confirm tie in points are within tolerance |  | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.7 | 2014-09-26 | Confirm piping tie-ins are complete and grout skid bases. Check and verify grouting is acceptable | I | YSP-2963-SOW-M-001, Manufacturers directions | AFC Drawings, Vendor IOM | Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 | NA | NA | H |  | W
4.8 | 2014-09-26 | Tension all hold down bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.9 | 2014-09-26 | Ensure no stress on nozzles from piping connection | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-011 | NA | NA | R |  | SV
4.10 | 2014-09-26 | Ensure preservation and maintenance as per manufacturer recommendation | I | YSP-2963-SOW-M-001 | Vendor IOM | Vendor IOM | NA | NA | W |  | R
5 |  | ASSEMBLY & VERIFICATION
5.1 | 2014-09-30 | Mechanical completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VP-00001, YA-2963-VC-00002 & Specifications | NA | NA | W |  | SV
5.2 | 2014-09-30 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VP-00001, YA-2963-VC-00002, Punchlist & Specifications | NA | NA | H |  | R
6 |  | INSPECTION & TESTING
6.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-004 | Not applicable | Approved ITP | NA | NA | R |  | R
6.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-004 | Not applicable | Approved ITP | NA | NA | W, H |  | R
6.3 | 2014-11-01 | Commission equipment in accordance with Commissioning Test Procedure | I | Commissioning Test Procedure, Manufacturers IOM | Commissioning Test Procedure, Manufacturers IOM | Approved CTP | NA | NA | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-005
ITP Number: |  | 01707-ITP-QA-005 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0007 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | DIESEL PUMPS SUPPLY AND INSTALLATION - YPP611A&B
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VM-00001, YA-2829-VM-00003, 00004, 00005 & Data Sheets | Not applicable | YA-2963-VM-00001, YA-2829-VM-00003, 00004, 00005, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply, confirming preservation intact after shipping | I | MTO; YA-2963-VM-00001, YA-2829-VM-00003, 00004, 00005; 01707-LST-ME-001 | YSP-2963-SOW-M-001, SS-M101 | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VM-00001, YA-2829-VM-00003, 00004, 00005, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | NA | NA | SV |  | R
4 |  | DIESEL PUMPS INSTALLATION | I
4.1 | 2014-09-20 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | SV
4.2 | 2014-09-20 | All footings shall be scabbled prior to install of equipment and structures | I | Vendor IOM, Scope of Work, | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | H
4.3 | 2014-09-20 | Install chemical anchors as per manufacturers directions | I | Vendor IOM, Scope of Work, Chemical Anchor IOM | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Chemical Anchor IOM, Survey Report (where required) | NA | NA | W |  | SV
4.4 | 2014-09-20 | Check that levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of each pump. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.5 | 2014-09-20 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required) | I | Construction Methodology (Schedule M of the Contract) | Australian Standards and Regulations | Certification, Approved Lift Study Report where required | NA | NA | H |  | W
4.6 | 2014-09-20 | Land each pump and confirm tie in points are within tolerance |  | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.7 | 2014-09-26 | Confirm piping tie-ins are complete and grout pump bases. Check and verify grouting is acceptable | I | YSP-2963-SOW-M-001, Manufacturers directions | AFC Drawings, Vendor IOM | Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 | NA | NA | H |  | W
4.8 | 2014-09-26 | Tension all hold down bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.9 | 2014-09-26 | Check alignment of drive/couplings Rotation Checked | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-009 or 01707-ITR-ME-010, 01707-ITR-017, Vendor IOM | NA | NA | H & R |  | R
4.10 | 2014-09-26 | Couplings Bolted, torqued and checked | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-009 or 01707-ITR-ME-010, 01707-ITR-017, Vendor IOM | NA | NA | H |  | R
4.11 | 2014-09-26 | Ensure no stress on nozzles from piping connection | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-009 or 01707-ITR-ME-010 | NA | NA | R |  | SV
4.12 | 2014-09-26 | Ensure preservation and maintenance as per manufacturer recommendation | I | YSP-2963-SOW-M-001 | Vendor IOM | Vendor IOM | NA | NA | W |  | R
5 |  | ASSEMBLY & VERIFICATION
5.1 | 2014-09-30 | Mechanical completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00001, YA-2829-VM-00003, 00004, 00005 & Specifications | NA | NA | W |  | SV
5.2 | 2014-09-30 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00001, YA-2829-VM-00003, 00004, 00005, Punchlist & Specifications | NA | NA | H |  | R
6 |  | INSPECTION & TESTING
6.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-005 | Not applicable | Approved ITP | NA | NA | R |  | R
6.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-005 | Not applicable | Approved ITP | NA | NA | W, H |  | R
6.3 | 2014-11-01 | Commission equipment in accordance with Commissioning Test Procedure | I | Commissioning Test Procedure, Manufacturers IOM | Commissioning Test Procedure, Manufacturers IOM | Approved CTP | NA | NA | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-008
ITP Number: |  | 01707-ITP-QA-008 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0015 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | DIESEL FILTERS SUPPLY AND INSTALLATION - YFR 617
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VM-00005, YA-2829-VM-00002 & Data Sheets | Not applicable | YA-2963-VM-00005, YA-2829-VM-00002, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply, confirming preservation intact after shipping | I | MTO; YA-2963-VM-00005, YA-2829-VM-00002; 01707-LST-ME-001 | YSP-2963-SOW-M-001, SS-M101 | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VM-00005, YA-2829-VM-00002, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | NA | NA | SV |  | R
4 |  | DIESEL FILTERS INSTALLATION | I
4.1 | 2014-09-20 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | SV
4.2 | 2014-09-20 | All footings shall be scabbled prior to install of equipment and structures | I | Vendor IOM, Scope of Work, | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | H
4.3 | 2014-09-20 | Install chemical anchors as per manufacturers directions | I | Vendor IOM, Scope of Work, Chemical Anchor IOM | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Chemical Anchor IOM, Survey Report (where required) | NA | NA | W |  | SV
4.4 | 2014-09-20 | Check that levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of filter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.5 | 2014-09-20 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required) | I | Construction Methodology (Schedule M of the Contract) | Australian Standards and Regulations | Certification, Approved Lift Study Report where required | NA | NA | H |  | W
4.6 | 2014-09-20 | Land filter and confirm tie in points are within tolerance |  | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.7 | 2014-09-26 | Confirm piping tie-ins are complete and grout filter bases. Check and verify grouting is acceptable | I | YSP-2963-SOW-M-001, Manufacturers directions | AFC Drawings, Vendor IOM | Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 | NA | NA | H |  | W
4.8 | 2014-09-26 | Tension all hold down bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.9 | 2014-09-26 | Ensure no stress on nozzles from piping connection | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-012 | NA | NA | R |  | SV
4.10 | 2014-09-26 | Ensure preservation and maintenance as per manufacturer recommendation | I | YSP-2963-SOW-M-001 | Vendor IOM | Vendor IOM | NA | NA | W |  | R
5 |  | ASSEMBLY & VERIFICATION
5.1 | 2014-09-30 | Mechanical completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00005, YA-2829-VM-00002 & Specifications | NA | NA | W |  | SV
5.2 | 2014-09-30 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00005, YA-2829-VM-00002, Punchlist & Specifications | NA | NA | H |  | R
6 |  | INSPECTION & TESTING
6.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-008 | Not applicable | Approved ITP | NA | NA | R |  | R
6.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-008 | Not applicable | Approved ITP | NA | NA | W, H |  | R
6.3 | 2014-11-01 | Commission equipment in accordance with Commissioning Test Procedure | I | Commissioning Test Procedure, Manufacturers IOM | Commissioning Test Procedure, Manufacturers IOM | Approved CTP | NA | NA | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-009
ITP Number: |  | 01707-ITP-QA-009 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0016 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: | SP-103 |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | DIESEL REFUELLING ARM SUPPLY AND INSTALLATION
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VM-00005, YA-2829-VM-00002 & Data Sheets | Not applicable | YA-2963-VM-00005, YA-2829-VM-00002, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply, confirming preservation intact after shipping | I | MTO; YA-2963-VM-00005, YA-2829-VM-00002; 01707-LST-ME-001 | YSP-2963-SOW-M-001, SS-M101 | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VM-00005, YA-2829-VM-00002, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | NA | NA | SV |  | R
4 |  | DIESEL REFUELLING ARM INSTALLATION | I
4.1 | 2014-09-20 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | SV
4.2 | 2014-09-20 | All footings shall be scabbled prior to install of equipment and structures | I | Vendor IOM, Scope of Work, | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | H
4.3 | 2014-09-20 | Install chemical anchors as per manufacturers directions | I | Vendor IOM, Scope of Work, Chemical Anchor IOM | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Chemical Anchor IOM, Survey Report (where required) | NA | NA | W |  | SV
4.4 | 2014-09-20 | Check that levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of refuelling arm. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.5 | 2014-09-20 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required) | I | Construction Methodology (Schedule M of the Contract) | Australian Standards and Regulations | Certification, Approved Lift Study Report where required | NA | NA | H |  | W
4.6 | 2014-09-20 | Land refuelling arm and confirm tie in points are within tolerance |  | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.7 | 2014-09-26 | Confirm piping tie-ins are complete and grout refuelling arm bases. Check and verify grouting is acceptable | I | YSP-2963-SOW-M-001, Manufacturers directions | AFC Drawings, Vendor IOM | Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 | NA | NA | H |  | W
4.8 | 2014-09-26 | Tension all hold down bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.9 | 2014-09-26 | Ensure no stress on nozzles from piping connection | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-012 | NA | NA | R |  | SV
4.10 | 2014-09-26 | Ensure preservation and maintenance as per manufacturer recommendation | I | YSP-2963-SOW-M-001 | Vendor IOM | Vendor IOM | NA | NA | W |  | R
5 |  | ASSEMBLY & VERIFICATION
5.1 | 2014-09-30 | Mechanical completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00005, YA-2829-VM-00002 & Specifications | NA | NA | W |  | SV
5.2 | 2014-09-30 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00005, YA-2829-VM-00002, Punchlist & Specifications | NA | NA | H |  | R
6 |  | INSPECTION & TESTING
6.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-009 | Not applicable | Approved ITP | NA | NA | R |  | R
6.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-009 | Not applicable | Approved ITP | NA | NA | W, H |  | R
6.3 | 2014-11-01 | Commission equipment in accordance with Commissioning Test Procedure | I | Commissioning Test Procedure, Manufacturers IOM | Commissioning Test Procedure, Manufacturers IOM | Approved CTP | NA | NA | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-010
ITP Number: |  | 01707-ITP-QA-010 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0017 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: | Piping Package |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | PIPING INSTALLATION - JUNCTION SOUTH WEST
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 & Data Sheets | Not applicable | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-06-01 | Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures | I | ITP, NDE procedures, Pressure testing procedures | Not applicable | Approved ITP’s NDE procedures, Pressure testing procedures | NA | NA | W, H |  | H
2.2 | 2014-06-01 | Submit Weld Procedure Specifications & Qualifications | I | WPS & WPQ Reports | ASME IX; AS1554; | Approved WPSs | NA | NA | H |  | H
2.3 | 2014-06-01 | Submit Welder Qualifications | I | Welder Qualification Reports & register | ASME IX; AS1554; | Approved Welder Qualifications | NA | NA | H |  | H
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply | I | Client MTO; YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022; 01707-LST-ME-001 | YSP-0000-SPE-M-001 (Section 8,9) | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records for Piping Works | NA | NA | SV |  | R
4 |  | MATERIALS PREPARATION
4.1 | 2014-09-17 | Mark materials for cutting & weld preparation. Dimensional check. | I | Piping Isometrics & structural detail drawings | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, 01707-ITR-ME-008 | NA | NA | SV |  | R
4.2 | 2014-09-17 | Prepare controlled/cut materials for fabrication | I | Material Control procedure, 01707-PLN-PM-002 | YSP-0000-SPE-M-001 (Section 2), AS4041 | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, 01707-ITR-ME-008 | NA | NA | SV |  | SV
4.3 | 2014-09-17 | Consumables Control | I | Consumable Control Procedure, 01707-PLN-PM-002 | YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1553 | Manufacturers Recommendations | NA | NA | SV |  | SV
5 |  | PRE-PROCESSING AND ASSEMBLY
5.1 | 2014-09-20 | Material allocation, Transfer & marking of heat numbers. Mark piping material to required length. Cut pipe sections to length in readiness for preparation, bevelling. | I | AFC Drawings, Material Control Procedure, and isometrics | AFC Drawings | Isometrics/Cutting List | NA | NA | SV |  | SV
5.2 | 2014-09-20 | Assembly of components prior to welding. Check: Fit-up & alignment, Root Gap & Landing, Install pipe Supports as per Drawing. | I | AFC Drawings, YSP-0000-M-001 | AFC Drawings, AS 4041, YSP-0000-M-001 | Isometrics/Cutting List | NA | NA | H |  | SV
5.3 | 2014-09-20 | Dimensional check prior to welding. | I | AFC Drawings, YSP-0000-M-001 |  | Isometrics/Cutting List | NA | NA | H |  | SV
5.5 | 2014-09-20 | Ensure Internals are clean and dry before welding. | I | AFC Drawings, YSP-0000-M-001 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-003 | NA | NA | SV |  | SV
5.6 | 2014-09-20 | Welding to be performed by qualified welder in accordance with approved welding Procedure Specification. | I | AFC Drawings, YSP-0000-M-001, WPS | AS 4041, YSP-0000-SPE-M-001 (Section 3) | Welder Qualification Records Welder Register | NA | NA | SV |  | SV
5.7 | 2014-09-20 | Carry out Welding of Joints , Field welds, Pipe supports & attachments. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 2) | Visual Inspection | NA | NA | H |  | W
5.8 | 2014-09-20 | Welding visual Inspection, Check: Root pass/weld size/profile & finish Closing weld size/profile & finish traceability records to be maintained, Welder, WPS Consumables etc. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 2) | 01707-ITR-ME-008, NDT Report | NA | NA | SV |  | SV
5.9 | 2014-09-20 | Weld repairs (if any) remove defect and re-weld in accordance with qualified procedure. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 2) | 01707-ITR-ME-007, 01707-ITR-ME-008, NDT Report | NA | NA | H |  | W
6 |  | INSPECTION AND TESTING
6.1 | 2014-10-05 | Dimensional check of piping assembly after welding "As Built" | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | As-Built Drawings | NA | NA | H |  | SV
6.2 | 2014-10-05 | 100% Final visual inspection of all welds and traceability check. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 2) | 01707-ITR-ME-007, 'As Built' Drawings | NA | NA | H |  | SV
6.3 | 2014-10-05 | Non Destructive Examination | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 4) | NATA endorsed Non Destructive Examination Reports | NA | NA | H |  | W
6.4 | 2014-10-05 | Carry out required Non Destructive Examination (NDE) as per Client specification requirements. Extent of, as per applicable to the appropriate "AS4041 Class piping " and Piping line lists. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 4) | NATA endorsed Non Destructive Examination Reports | NA | NA | H |  | W
7 |  | PIPE INSTALLATION - BOLTED JOINTS
7.1 | 2014-09-20 | Inspect nozzle integrity on all static and rotating equipment to which pipe spools are connected. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-001 | NA | NA | W |  | SV
7.2 | 2014-09-20 | Ensure Internals are clean and dry prior to assembly. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-001 | NA | NA | H |  | SV
7.3 | 2014-09-20 | Shim steelwork at pipe support locations and survey for correct elevation. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-001, Visual Inspection or Survey results | NA | NA | H/R |  | SV
7.4 | 2014-09-20 | Assembly - Install pipework Align mating flange joints to specified tolerances - To mechanical equipment. - To static equipment. - pipe to pipe. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-001, Isometrics | NA | NA | H |  | W
7.5 | 2014-09-20 | Install in line piping components gaskets, nuts, bolts and Instrumentation. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-001, Isometrics, Material certificates | NA | NA | H |  | SV
7.6 | 2014-09-20 | Check valves & instrumentation for Identification tags & check orientation. install valves and instrumentation. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | P&ID's | NA | NA | W |  | R
7.7 | 2014-09-20 | Ensure correct bolts are installed & tensioned. | I | AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 3) | 01707-ITR-ME-001, Isometrics, Torque Wrench Calibration Report | NA | NA | R |  | SV
8 |  | PRESSURE TESTING (WHERE APPLICABLE)
8.1 | 2014-10-20 | Develop Hydrostatic or Pneumatic Pressure Test Packs. Check NDE & Calibration Certificates prior to testing. | I | Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 4) | System Test Pack | NA | NA | H |  | W
8.2 | 2014-10-20 | Flush clean piping system. The cleaning media shall be as per testing media detailed on the line List. | I | Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 4) | NATA Certified Pressure Test Report and Graph | NA | NA | W |  | SV
8.3 | 2014-10-20 | Pressure Test Pipework 'Witness Test for any leaks'. | I | Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 4) | 01707-ITR-ME-005 | NA | NA | H |  | W
8.4 | 2014-10-20 | Verification of cleanliness & dryness. | I | Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018 | AS 4041, YSP-0000-SPE-M-001 (Section 4) | 01707-ITR-ME-005 | NA | NA | W |  | SV
10.5 | 2014-10-20 | Pickling/Chemical Treatment | I | YSP-0000-SPE-M-001 (Section 2.5) | YSP-0000-SPE-M-001 (Section 2.5), ASME IX, AS1627 Part 5 | Subcontractor repair; 01707-ITR-ME-003 | NA | NA | H |  | W
9 |  | SURFACE TREATMENT (TOUCH UPS)
9.1 | 2014-10-30 | Protect surfaces not requiring treatment, e.g. Field welds. nameplates. machined surfaces. | I | SS-P120 | SS-P120 | Visual Inspection | NA | NA | SV |  | SV
9.2 | 2014-10-30 | Check the blast medium is to the specifications. | I | SS-P118_2 (Section 7) | SS-P118_2 (Section 7) | Surface Treatment Records | NA | NA | SV |  | SV
9.3 | 2014-10-30 | Check surface cleaning as per specification | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | SV |  | SV
9.4 | 2014-10-30 | Monitor atmospheric conditions daily for Temperature (> 5 •c and <50 •c) and Humidity (>20% and <85%) | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | SV |  | SV
9.5 | 2014-10-30 | Check item to be painted (piping I steelwork etc.) for defects, damage. No welding flux, splatter, sharp edges etc. Confirm all inspections, NDT etc. on the item have been completed prior to painting. | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | H |  | SV
9.6 | 2014-10-30 | Ensure the items to be painted are adequately laid out and masked as needed | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | SV |  | SV
9.7 | 2014-10-30 | Check correct paint is being used | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | R |  | SV
9.8 | 2014-10-30 | Ensure paints are mixed as per manufacturers recommendation | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | SV |  | SV
9.9 | 2014-10-30 | Check application is correct and is free of paint runs and other defects | I | SS-P118_2 (Section 9) | SS-P118_2 (Section 9) | Surface Treatment Records | NA | NA | SV |  | SV
11 |  | ASSEMBLY & VERIFICATION
11.1 | 2014-11-01 | Piping completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-M-001 (Section 8,9) | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022 & Specifications | NA | NA | SV |  | SV
11.2 | 2014-11-01 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-M-001 (Section 8,9) | YA-2963-VP-00001, 00002, 00003, YA-2829-VP-00001, 00002, 00003, 00022, Punchlist & Specifications | NA | NA | H |  | R
11.3 | 2014-11-02 | Review completed ITP | I | 01707-ITP-QA-010 | Not applicable | Approved ITP | NA | NA | SV, R |  | R
11.4 | 2014-11-03 | Final Inspection | I | Inspection release form | Primero Form | Delivery Documentation | NA | NA | W, H |  | R
11.5 | 2014-11-01 | Commission equipment in accordance with Commissioning Test Procedure | I | Commissioning Test Procedure, Manufacturers IOM | Commissioning Test Procedure, Manufacturers IOM | Approved CTP | NA | NA | W, H |  | SV
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-011
ITP Number: |  | 01707-ITP-QA-011 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0018 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | 0 | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | STRUCTURAL STEELWORK AND PIPE SUPPORTS INSTALLATION - JC
Works Locations: |  | JC
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
1.2 | 2013-11-11 | Review Drawings & Data Sheets | I | YA-2963-VM-00003, 00004 & Data Sheets | Not applicable | YA-2963-VM-00003, 00004, VDDI | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP, NDE procedures | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
2.2 | 2014-08-01 | Submit Weld Procedure Specifications & Qualifications | I | WPS & WPQ Reports | ASME IX; AS1554; | Approved WPSs | NA | NA | H |  | R
2.3 | 2014-08-01 | Submit Welder Qualifications | I | Welder Qualification Reports & register | ASME IX; AS1554; | Approved Welder Qualifications | NA | NA | H |  | R
3 |  | MATERIALS
3.1 | 2014-09-15 | Monitor Incoming Materials (New) And Client supply, confirming preservation intact after shipping | I | MTO; YA-2963-VM-00003, 00004; 01707-LST-ME-001 | YSP-0000-SPE-S-002 (Section 4) | Signed Delivery Dockets; Material Certificates, Inspection Certificates | NA | NA | SV, W |  | SV
3.2 | 2014-09-15 | Material Traceability | I | YA-2963-VM-00003, 00004, Material Control Procedure, and Client Specifications | Materials Specifications | Traceability Records | NA | NA | SV |  | R
4 |  | STRUCTURAL STEELWORK AND PIPE SUPPORTS INSTALLATION | I
4.1 | 2014-09-20 | Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | SV
4.2 | 2014-09-20 | All footings shall be scabbled prior to install of equipment and structures | I | Vendor IOM, Scope of Work, | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Survey Report (where required) | NA | NA | W |  | H
4.3 | 2014-09-20 | Install chemical anchors as per manufacturers directions | I | Vendor IOM, Scope of Work, Chemical Anchor IOM | AFC Drawings, Vendor IOM | 01707-ITR-ME-013, MSDS, Chemical Anchor IOM, Survey Report (where required) | NA | NA | W |  | SV
4.4 | 2014-09-20 | Check that levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of each item. | I | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.5 | 2014-09-20 | Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required) | I | Construction Methodology (Schedule M of the Contract) | Australian Standards and Regulations | Certification, Approved Lift Study Report where required | NA | NA | H |  | W
4.6 | 2014-09-20 | Land each item and confirm tie in points are within tolerance |  | Vendor IOM, Scope of Work | AFC Drawings, Vendor IOM | 01707-ITR-ME-011, 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.7 | 2014-09-23 | Erect walkway columns and beams. | I | Construction Methodology (Schedule M of the Contract) | AS 4100, YSP-0000-S-002, Approved Drawings | 01707-ITR-ME-006 Survey Report (where required) | NA | NA | W |  | SV
4.8 | 2014-09-23 | Structure Installed and checked (Location/ Elevation/ level) Snug tighten Primary connections throughout the structure | I | Construction Methodology (Schedule M of the Contract) | AS 4100, YSP-0000-S-002 | Visual Inspection or Survey Report (where required) | NA | NA | H |  | W
4.9 | 2014-09-23 | Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-006, Survey Report | NA | NA | W |  | SV
4.10 | 2014-09-23 | Tension all secondary steel bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.11 | 2014-09-26 | Grating and handrails to be installed as required to ensure safe work practice and access. | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-006, Survey Report | NA | NA | W |  | SV
4.12 | 2014-09-26 | Confirm piping tie-ins are complete and grout items and walkways. Check and verify grouting is acceptable | I | YSP-2963-SOW-M-001, Manufacturers directions | AFC Drawings, Vendor IOM | Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 | NA | NA | H |  | W
4.13 | 2014-09-26 | Tension all hold down bolts and nuts | I | Construction Methodology (Schedule M of the Contract) | AS 4100 Approved Drawings | 01707-ITR-ME-015, Survey Report | NA | NA | W |  | SV
4.14 | 2014-09-26 | Ensure no stress on nozzles from piping connection | I | YSP-2963-SOW-M-001, SS-M101 | AFC Drawings, SS-M101, Vendor IOM | 01707-ITR-ME-011 | NA | NA | R |  | SV
4.15 | 2014-09-26 | Ensure preservation and maintenance as per manufacturer recommendation | I | YSP-2963-SOW-M-001 | Vendor IOM | Vendor IOM | NA | NA | W |  | R
5 |  | ASSEMBLY & VERIFICATION
5.1 | 2014-09-30 | Structural and mechanical completion and verification | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00003, 00004 & Specifications | NA | NA | W |  | R
5.2 | 2014-09-30 | Punch listing completed | I | Construction Methodology (Schedule M of the Contract) | YSP-0000-SPE-S-002 (Section 11) | YA-2963-VM-00003, 00004, Punchlist & Specifications | NA | NA | H |  | R
6 |  | INSPECTION & TESTING
6.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-011 | Not applicable | Approved ITP | NA | NA | R |  | R
6.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-011 | Not applicable | Approved ITP | NA | NA | W, H |  | R
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-015
ITP Number: |  | 01707-ITP-QA-015 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0022 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | C | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | CIVIL WORKS
Works Locations: |  | JC
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
3 |  | PREPARATION
3.1 | 2014-10-01 | Obtaining Clearing Permit | S | Environmental Management Plan | Once | Clearing Permit | H |  | H |  | H
3.2 | 2014-10-01 | Approved and issued permission to work | S | All relevant permissions obtained | Signed and issued | Excavation permission, Signed ITP | W |  | W |  | H
3.3 | 2014-10-01 | Liaising with Shutdown Coordinator | S | Calibre supervisor for Timing of Works | Visual Inspection | Signed ITP | H |  | H |  | W
3.4 | 2014-10-10 | Barricading | S | Directed by Calibre Representative | Visual Inspection | Signed ITP | W |  | W |  | V
3.5 | 2014-10-10 | Survey to set out extents of works for excavations | S | Supervisor; IFC Drawings | Survey set-out | ·Survey Marks placed, ITP, Inspection Release Certificate | H |  | H |  | W
3.6 | 2014-10-10 | Clear and Grub designated area | S | Clear and Grub vegetation from work site as directed | Visual Inspection |  | V |  | V |  | W
4 |  | EXCAVATION
4.1 | 2014-10-10 | Trenching to be large enough to accommodate the pipe and allow compaction of the backfill | S | As per IFC Drawings, YSP-0000-SPE-Y-003 - Section 14 | Visual Inspection | Signed ITP | W |  | W |  | V
4.2 | 2014-10-10 | Install services - piping, electrical etc and perform testing as required (e..g. hydrotesting) | I | As per IFC Drawings, YSP-0000-SPE-Y-003, refer services ITP | As per individual service ITP/ITR | Signed ITPs/ITRs | W |  | W |  | V
4.3 | 2014-10-10 | Complete as-built survey of services | S | As per IFC Drawings | Survey set-out | ·Survey reports | W |  | W |  | V
5 |  | BACKFILL AND COMPACT
5.1 | 2014-10-10 | Source, Source, place, compact and fill suitable suitable bedding material | S | PE/Supervisor, YSP-0000-SPE-Y-003 section 20 | Visual Inspection, density tests as applicable (93% compaction) | Signed ITP, 01707-ITR-ME-002, density reports (section 26 of YSP-0000-SPE-Y-003 | V |  | V |  | V
5.2 | 2014-10-10 | Source, place, compact and fill suitable backfill (non-trafficable) material where applicable | S | PE/Supervisor, YSP-0000-SPE-Y-003 section 20 | Visual Inspection, density tests as applicable (93% compaction) | Signed ITP, 01707-ITR-ME-002, density reports (section 26 of YSP-0000-SPE-Y-003 | V |  | V |  | V
5.3 | 2014-10-10 | Source, place, compact and fill suitable backfill (trafficable) material where applicable | S | PE/Supervisor, YSP-0000-SPE-Y-003 section 20 | Visual Inspection, density tests as applicable (93% compaction) | Signed ITP, 01707-ITR-ME-002, density reports (section 26 of YSP-0000-SPE-Y-003 | V |  | V |  | V
5.4 | 2014-10-10 | Source, place, compact and fill suitable backfill (top 300 under roads/hardstand) material where applicable | S | PE/Supervisor, YSP-0000-SPE-Y-003 section 20 | Visual Inspection, density tests as applicable (93% compaction) | Signed ITP, 01707-ITR-ME-002, density reports (section 26 of YSP-0000-SPE-Y-003 | V |  | V |  | V
6 |  | FINISHING AND CLEAN UP
6.1 | 2014-10-10 | Site Clean up | S | PE/Supervisor, YSP-0000-SPE-Y-003 | Visual Inspection | Signed ITP | V |  | V |  | V
7 |  | INSPECTION & TESTING
7.1 | 2014-10-15 | Review completed ITP | I | 01707-ITP-QA-015 | Not applicable | Approved ITP | R |  | R |  | R
7.2 | 2014-10-15 | Final Inspection | I | 01707-ITP-QA-015 | Not applicable | Approved ITP | W, H |  | W, H |  | R
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-016
ITP Number: |  | 01707-ITP-QA-016 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0022 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | C | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | CONCRETE WORKS
Works Locations: |  | JC/JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[7 empty] | Subcontractor | Sign | Contractor | Sign | Engineer | Sign
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 |  | DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | Review Scope of Work and associated specifications | I | Client SOW: YSP-2963-SOW-M-001 | Not applicable | Contract Document | NA | NA | W |  | SV
2 |  | APPROVALS
2.1 | 2014-08-01 | Submit Project Documentation, ITP | I | ITP | Not applicable | Approved ITP’s | NA | NA | W, H |  | H
3 |  | PRELIMINARIES
3.1 | 2014-11-01 | Concrete Mix Design. | I | RTIO SS-C107 Design drawings | Concrete Mix Design Approved by Superintendant. | Batch plant documentation | N/A | N/A | H |  | H
3.2 | 2014-11-01 | Reinforcement – Supply. | I | RTIO SS-C108-53 | Copies of the reinforcement supplier’s certification that reinforcing complies to AS4671 & ACRS. Certificates shall be included in MDR | Certificates | N/A | N/A | H |  | R
4 |  | CONSTRUCTION
4.1 | 2014-11-07 | Setting out | I | PGr Work Procedure | The structure must be set out by a surveyor prior to the placement of formwork and reinforcement. | Survey | N/A | N/A | H |  | H
4.2 | 2014-11-07 | Preparation of Ground Under Slabs. | I | RTIO SS-C108 Design drawings | Builders Film (Waterproof Membrane) is present and intact under all slabs. Or Blinding concrete is in situ | Visual. | N/A | N/A | W |  | SV
4.3 | 2014-11-07 | Preparation of Lean Mix Blinding Under Pad Footings. | I | PGr Work Procedure | Blinding surface is clean, free from foreign substances and thoroughly wetted immediately prior to placement of concrete. | Visual. | N/A | N/A | SV |  | SV
4.4 | 2014-11-07 | Preparation of Construction Joints. | I | RTIO SS-C108 PGr Work Procedure | Construction joints to be suitably scabbled. Construction joint surface is clean, free from foreign substances and thoroughly wetted immediately prior to placement of concrete. | Visual. | N/A | N/A | SV |  | SV
4.5 | 2014-11-07 | Formwork - Placement | I | RTIO SS-C108-7 PGr Work Procedure | Formwork to be placed as per survey set out and accurately and safely secured. Formwork shall not be placed in locations where reinforcement and other elements cannot be inspected. Prior to placing reinforcement a release agent has been applied to the face of the formwork compatible with the required surface finish. | Visual | N/A | N/A | SV |  | SV
4.6 | 2014-11-07 | Formwork Placement – Prefabricated | I | RTIO SS-C108-7 PGr Work Procedure | Prefabricated Formwork to be dimensionally checked by aN engineer or surveyor prior to being lifted into position. | Survey | N/A | N/A | SV |  | SV
4.7 | 2014-11-07 | Formwork Inspection | I | RTIO SS-C108-7 PGr Work Procedure | Formwork has been constructed in accordance with the submitted formwork design, is clean, to correct lines and levels and will result in required surface finish being met. | Visual. | N/A | N/A | SV |  | SV
4.8 | 2014-11-07 | Reinforcement – Handling and Storage | I | RTIO SS-C108-8 PGr Work Procedure | Reinforcement shall be clean and free from dust, oil, grease etc. | Visual. | N/A | N/A | SV |  | SV
4.9 | 2014-11-07 | Setting out of Reinforcement | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | The structure must be set out prior to the placement of reinforcement. | Visual. | N/A | N/A | SV |  | SV
4.1 | 2014-11-07 | Welding of Reinforcement | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | Details of any welded joint other than those specifically nominated on the design drawings are to be submitted to the Superintendents Representative prior to welding. Welding not to take place unless approval for welded joints has been received. Approved welding to be in accordance with AS1554.3 | Verify. | N/A | N/A | H |  | H
4.11 | 2014-11-07 | Reinforcement – Installation | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | Reinforcement to have minimum clear cover as shown as shown on the drawings, and to be within tolerances | Visual. | N/A | N/A | W |  | SV
4.12 | 2014-11-07 | Reinforcement – Supports | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | Plastic chairs or mortar block spacers shall be used for reinforcement supports. Mortar block spacers shall have properties at least equal to the surrounding concrete. | Visual. | N/A | N/A | W |  | SV
4.13 | 2014-11-07 | Cast-Ins / Block-outs – Planning | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | Cast-Ins to be checked on plans prior to pours. | Verify | N/A | N/A | H |  | W
4.14 | 2014-11-07 | Cast-Ins / Block-outs – Placement | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | Cast-ins shall be within tolerances 3mm nominated in the specifications & design drawings. Position and fastening to be checked prior to placement of concrete. | Survey / Visual. | N/A | N/A | H |  | W
4.15 | 2014-11-07 | Reinforcement inspection | I | RTIO SS-C108-8 PGr Work Procedure Design drawings | PGr to carry out inspection ensuring reinforcement meets design specification. | Survey / Visual. | N/A | N/A | SV |  | R
4.16 | 2014-11-07 | Concrete Placement – General | I | RTIO SS-C108-9 PGr Work Procedure Design drawings | A pre-pour notice form (see appendix B of Specification) shall be filled out and submitted to the Superintendent giving 24 hours notice of the intention to place concrete. Work out of daylight hours shall only occur with consent by the Superintendents Representative. | Visual / Documentation Concrete Pour Checklist | N/A | N/A | H |  | H
4.17 | 2014-11-07 | Concrete Placement – Weather Conditions | I | RTIO SS-C108-9 | Concrete shall not be placed when ambient temperature is lower than 5°C. Pours during adverse weather conditions shall not take proceed. Each pour to be assed and the Superintendents Representative and PGr Project Manager to be in agreement as to whether or not the pour is to continue. | SER to verify with PGr PM when conditions are adverse. | N/A | N/A | H |  | SV
4.18 | 2014-11-07 | Concrete mix | I | AS 3973, AS3600 RTIO SS-C107 | Concrete mix design shall be in accordance with the Project Specification. All dockets showing mix design ingredients shall be retained by PGr Site Engineer. | Verify / Testing. | W |  | H |  | SV
4.19 | 2014-11-07 | Concrete Slump | I | AS1012 RTIO SS-C107 | Concrete slump shall be As per the design specification / Quality Plan (80mm +/- 15mm). | Verify / Testing. | W |  | H |  | SV
4.2 | 2014-11-07 | Concrete Placement – Concrete Temperature | I | RTIO SS-C107 | The temperature of concrete, measured immediately prior to placement, shall not be greater than 320C | Verify / Testing | W |  | SV |  | SV
4.21 | 2014-11-07 | Concrete Placement – Discharge | I | RTIO SS-C108-10 | Concrete shall be incorporated into works within 60 minutes of batching. Discharge shall occur at a maximum drop height of 2m. | Verify | W |  | H |  | SV
4.22 | 2014-11-07 | Concrete Placement – Construction Joint | I | RTIO SS-C108-10 | Construction Joints shall be moistened with a water or slurry mix prior to placement of concrete | Verify | N/A | N/A | H |  | SV
4.23 | 2014-11-07 | Concrete Placement – Compaction | I | RTIO SS-C108-10 | Vibration shall be applied to the full depth of each layer of concrete and extend into the top 150mm of the underlying layer. Concrete shall not be placed in layers exceeding 300mm. | Verify | N/A | N/A | W |  | SV
4.24 | 2014-11-07 | Concrete Placement – Surface Finish | I | RTIO SS-C108 | Surfaces of concrete shall have class 5 finish on unexposed surfaces. Exposed surfaces shall be of class 3 finish for vertical surfaces. Finish for Horizontal shall be finished with a non- slip finish as directed by the plans or superintendent. | Visual | N/A | N/A | H |  | SV
4.25 | 2014-11-07 | Concrete Placement – Curing | I | RTIO SS-C108-10 | Concrete to be sufficiently cured using an approved curing compound as per the manufacturers specification. | Visual | N/A | N/A | SV |  | SV
4.26 | 2014-11-07 | Concrete Testing | I | RTIO SS-C107 | All concrete testing must be to the frequencies set out in table 25.2 in the specification & section of this ITP. All records must be kept with relevant information and copies of all tests to be passed on to the superintendent within 7 days of the tests been completed. | Verify / Testing | W |  | R |  | R
4.27 | 2014-11-07 | Formwork Removal | I | RTIO SS-C108-7.6 | Formwork removed as per the references to left. | 24 hours (minimum) after placement of concrete | N/A | N/A | W |  | SV
4.28 | 2014-11-07 | Concrete Strength | I | AS 3600 | Concrete has reached specific 28 Day Design Strength according to NATA test lab results. | NATA test lab. | W |  | SV |  | SV
4.29 | 2014-11-07 | As Built - Tolerances | I | AS3600 Table 4.4.2 | Concrete, HD Bolts, embedded items etc. shall conform to the project drawings and specification and any changes to be noted on as constructed drawings & forwarded to RTIO. | Survey | N/A | N/A | H |  | SV
4.3 | 2014-11-07 | Defects | I | RTIO SS-108-12 | Defects to be marked on drawings and attached to ITP. For list of possible defects refer to RTIO spec | Visual. | N/A | N/A | H |  | W
5 |  | INSPECTION & TESTING
5.1 | 2014-10-15 | Review completed ITP | I | Approved ITP-016 | Not applicable | Approved ITP | R |  | R |  | R
5.2 | 2014-10-15 | Final Inspection and Finalise MDR | I | Approved ITP, Appendix D of YSPA1034 | Not applicable | Approved ITP | W, H |  | W, H |  | R
NOTES: | 1 | CLIENT SHALL BE GIVEN 72 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;