## ITP-001
ITP Number: | 01743-ITP-PLN-002 | Client Contract Number: |  | Contract Item Number: |  |  |  | Legend: | W = Witness | S = Subcontractor | I = In House
Revision Number: | A | Subcontractor | PIVS Engineering | Equipment Number: | Piping Works |  |  |  | H = Hold | VM = Verification Monitoring | R = Review
Contractor: | Primero Group | Description of Service: | PIPING SUPPLY AND FABRICATION – FIRE WATER
Works Locations: | Fabrication Workshop
Task Number | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements
[6 empty] | Sub Contractor | Sign | Contractor | Sign | RTIOP Representative | Sign
1 | 3 | 4 | 5 | 6 | 7 |  |  | 8 | 9 | 10 | 11
1 | DESIGN/SPECIFICATIONS
1.1 | Review Scope of Work and associated specifications | S | SOW 01743-SOW-PM-001 | Client Specifications | Contract Documents |  | W | W |  | W
1.2 | Review Drawings & Data Sheets | S | AFC Drawings, Client Specifications | Client Specifications | AFC Drawings |  | W | W |  | W
2 | APPROVALS
2.2 | Submit Weld Procedure Specifications & Qualifications | S | Welding Procedure Specifications: Welding Procedure Qualification Records | AS4041 | Approved WPS |  | H | H |  | H
2.3 | Submit Welder Qualifications | S | Welder Qualification Records | AS1554 | Approved Welder Qualifications |  | H | H |  | H
4 | MATERIALS
4.1 | Monitor Incoming Materials | S | SOW 01743-SOW-PM-002 | Visual Inspection | Contractor BOM Document: 01743-BOM-LST-001 |  | W | W |  | VM
4.2 | Check for imperfections in flanges such as gouges and/or protrusions in the serations on gasket sealing faces | S | SOW 01743-SOW-PM-002 | Visual Inspection | Material Traceability Forms Material Certificates |  | W | R |  | VM
4.3 | Store materials and welding consumable to eliminate damage | S | SOW 01743-SOW-PM-003 | Visual Inspection | Material Certificates: |  | W | VM |  | VM
4.4 | Material Traceability | S | 01743-LST-PC-001_A Manufacturing Data Report Index | Visual Inspection | Material Traceability Forms Material Certificates |  | W | VM |  | VM
6 | FABRICATION - PIPING
6.1 | Mark materials for cutting & weld preparation. Dimensional check. | S | AFC Isometric Drawings | SS-M120 Specification | AS Built AFC Isometric Drawings |  | W | W |  | VM
6.2 | Assemble material components as per drawing. | S | AFC Isometric Drawings | SS-M120 Specification | AS Built AFC Isometric Drawings |  | W | VM |  | VM
6.3 | Assembly of components prior to welding. Check fit-up, alignment and root gap. | S | AFC Isometric Drawings | SS - M120 Specification | AS Built AFC Isometric Drawings |  | H | H |  | W
6.4 | Welding of assembled components | S | Welding Procedure Specifications | Welder Qualification Records | Weld Map (Weld and NDT Traceability): Welding Procedure Qualification Records: |  | W | W |  | VM
6.5 | Ongoing visual weld inspection of all welded components. | S | Welding Procedure Specifications | Welder Qualification Records: | Weld Map (Weld and NDT Traceability): Welding Procedure Qualification Records: |  | H | H |  | W
8 | INSPECTION & TESTING - PIPING
8.1 | Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc | S | AFC Isometric Drawings | SS-M120 Specification | AFC Isometric Drawings |  | H | W |  | W
8.2 | NDE in accordance with approved drawings, specifications | S | NDT Procedures | SS-M120 Specification | NDT Reports |  | H | W |  | W
8.3 | Weld repairs | S | Weld Repair Procedure: | Welder Qualification Records | Weld Map (Weld and NDT Traceability): Welding Procedure Qualification Records: |  | H | H |  | W
8.6 | Pipe Cleanliness | S | SOW 01743-SOW-PM-003 | Visual Inspection | Spool cleanliness and drying summary: 06301-ITR-ME-003 |  | H | H |  | W
10 | SURFACE TREATMENT - GALVANISING
10.1 | Ensure no unvented, closed or blind sections exist in any assembly (holes shall not be cut without prior approval) | S | SS-P118 Painting Specification | Visual Inspection | Coating Inspection Report |  | W | VM |  | VM
10.2 | Cleaning of all surfaces to be galvanised by pickling | S | SS-P118 Painting Specification | Visual Inspection | Coating Inspection Report |  | W | VM |  | VM
10.3 | Hot dip galvanising | S | SS-P118 Painting Specification | Visual Inspection | Coating Inspection Report |  | W | VM |  | VM
10.4 | Remedial work as required and Re-inspection | S | SS-P118 Painting Specification | Visual Inspection | Coating Inspection Report |  | W | VM |  | VM
10.5 | Final Inspection | S | SS-P118 Painting Specification | Visual Inspection | Coating Inspection Report |  | H | H |  | W
13 | FINALISE DOCUMENTATION
13.3 | MDR to be progressively compiled and submitted to client for final approval | S | SOW 01743-SOW-PM-003 | 01743-IND-PM-001 | Manufacturer’s Data Book |  | H | H |  | W
13.4 | Final Inspection | S | Inspection Checklists; | SOW 01743-SOW-PM-003 | Primero Inspection Release Certificate: |  | H | H |  | W
13.5 | Preparation & packaging for transport & load out to site, ensuring packaging will limit chance of condensation and flash corrosion of pipe internals by using sealed end caps | S | SOW 01743-SOW-PM-003 | Detailed Packing List: 01743-LST-PC-001 | CAPL Inspection Release Certificate: |  | H | H |  | W
NOTES: | CLIENT SHALL BE GIVEN 48 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY FOR WITNESS AND HOLD POINTS;