| Client: |  |  | Contract No: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Project: |  |  | Document No: |  |  | Revision: |  |
| Area/System No: |  |  | Area/System Description: |  |  |  |  |

| Reference Document |  |  | Controlling Document |  |  | Verifying Documents |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | Title |  | No. | Title |  | No. | Title |
|  | BGER Project Quality Management Plan (PQMP) |  | AS/NZS2033 | Installation of polyethylene pipe systems |  |  | Material Certificates |
| AS 4041 | Pressure Piping |  | AS/NZS4129 | Fittings for polyethylene pipes |  | BGER-QA-CHL-0001 | Material Inspection Report |
|  | Weld Procedure Specifications (WPS) |  | AS/NZS4130 | Polyethylene pipes for pressure applications |  |  | Approved Lift Studies |
|  | Welder Qualification Register (WQR) |  | PMBWELD 301B/302B |  |  |  | Survey Report |
|  |  |  | PIPA POP001/003 |  |  | BGER-QA-CHL-xxxx | Polyethylene Piping Installation Checklist |
|  |  |  |  |  |  |  | Weld Map |
|  |  |  | BGER-QA-WOR-0009 | Hydrostatic Testing Work Instruction |  | BGER-QA-CHL-3002 | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist |
|  |  |  |  | AFC Drawings |  | BGER-QA-CHL-3003 | Flange Bolting Checklist |
|  |  |  |  | Client’s specifications |  | BGER-QA-CHL-0002 | Coating & Surface Treatment Checklist |

| Legend |  |  | Approval and Change History |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Verification Activity |  |  | Rev | Details | Date | Prepared by (BGER) | Client Approval (XXX) |
| H – Hold Point | Work shall not proceed past the Hold Point until released by the Organisation imposing the Hold Point. 48 hrs. notice required. |  |  |  |  |  |  |
| W – Witness Point | An Inspection Point that may be witnessed by the Organisation imposing the Witness Point. 48 hrs. notice required. |  |  |  |  |  |  |
| I – Inspection | Formal inspection activity to be undertaken and recorded. |  |  |  |  |  |  |
| S – Surveillance | An activity that is subject to on-going monitoring |  |  |  |  |  |  |
| R – Review | Review of text reports/records or other evidence of compliance. |  |  |  |  |  |  |
| Responsible Person (RP) |  |  |  |  |  |  |  |
| SUP | Supervisor |  |  |  |  |  |  |
| QR | Quality Representative (Project Engineer) |  |  |  |  |  |  |
| SUR | Surveyor |  |  |  |  |  |  |
| NDTT | NDT Technician |  |  |  |  |  |  |

| Item | Activity/Operations/Stage No. | Controlling Document/Procedure | Standard, Spec, Drawing Ref or Acceptance Criteria | Verifying Document/Report/ Certificate | Verification Activity by |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | BGER RP | BGER/ sign | Client/ sign |  |
|  | Approvals |  |  |  |  |  |  |  |
|  | Prepare BGER’s ITP to suit and submit to Client for approval | PQMP | ITP | Approved ITP | QR | H | H |  |
|  | Submit and obtain approval for Weld Procedure Specifications and Welder Qualifications | PQMP | POP001 / POP003 PMBWELD301B / 302B | Approved WPS and WQR WPS and WQR Register | QR | H | H |  |
|  | Confirm all required critical and heavy Lifts are identified. Prepare Lift Studies to suit and submit to Client for Approval. | PQMP | ITP | Approved Lift Studies (if required) | QR | H | H |  |
|  | Confirm that the respective procedures & acceptance criteria (as required) for Cleaning, Hydro-Testing, Drying & Preservation of the Pipe System be prepared and submitted to Client for approval | PQMP | AS/NZS 2033, Client’s specs | Approved Pipe Cleaning Procedure, Approved Pipe Hydro-Testing Procedure, Approved Pipe Drying Procedure, Approved Pipe Preservation procedure | QR, SUP | H | H | Submit procedures as required depending on the size and service of the pipe system |
|  | Area handover and acceptance | PQMP | ITP | Contract Requirement | QR | H | H |  |
|  | Material Receipt |  |  |  |  |  |  |  |
|  | Check material for damage due to delivery and fabrication defect | PQMP AS/NZS4129 AS/NZS4130 | Isometric drawings, Delivery Packing List | Material Inspection Report | QR | I, R | R |  |
|  | Confirm correct material received | PQMP | AFC Drawings | Material Certificates | QR | I, R | R |  |
|  | Check that correct quantities and dimensions of material and welding consumables are delivered | PQMP | Isometric drawings, Bill of Material | Material Inspection Report, Welding Consumables Material Certificates | QR | I, R | R |  |
|  | Verify that the pipes, fittings and spools are marked with identification numbers/ codes as per the approved Isometric drawings (and Piping & Instrument Diagram) | PQMP | Isometric drawings, Bill of Material, Process & Instrument Diagram (P&ID) | Material Inspection Report | QR | I, R | S |  |
|  | Confirm that the materials are stored in a controlled area. | PQMP | ITP | Material Receipt Checklist | QR | I, R | S |  |
|  | Survey and Equipment set up |  |  |  |  |  |  |  |
|  | Verity that the elevations, coordinates and orientation for the piping route is surveyed and marked correctly. | PQMP | Isometric Drawings, Survey control points | Survey Report | SUR | I, H | R |  |
|  | Verify that the pipe racks, trenches, road crossings (open cut or tunnel) are readied for aligning the pipe. Verify that sufficient space (or temporary spool) has been allowed between pipes for installation of valve stems and actuators. | PQMP | Isometric Drawings, AFC drawings | Polyethylene Piping Installation Checklist | QR | I | R |  |
|  | Check and confirm that all owned/hired required plant and equipment are available and calibrated (where required). | PQMP | Project Execution Plan | Calibration Certificates | QR | I | R |  |
|  | Polyethylene Piping Installation |  |  |  |  |  |  |  |
|  | Verify that all lines are straight and plumb (except where it is specified otherwise In the Isometric drawing) | PQMP | Isometric Drawings, Client’s specs | Polyethylene Piping Installation Checklist | SUP | S | S |  |
|  | Verify that the required pipe supports, saddles, pipe racks, etc. are correctly erected according to client’s specs | PQMP | Isometric Drawings, Client’s specs, AS/NZS 2033 | Polyethylene Piping Installation Checklist | SUP | S | S |  |
|  | Verify that all welding conform to standards and Client’s specs, Welder ID is correctly marked and recorded on Weld Map. | WPS, WQR | POP001 / POP003, PMBWELD 301B / 302B, Client’s specs | Weld Map | QR | I | S |  |
|  | Visual examination of 100% of welds | PQMP | POP001 / POP003, Industry guidelines | Polyethylene Piping Installation Checklist | QR | H | R |  |
|  | Flange and valve connections free of stress and orientated correctly. | AS/NZS2033 | AS/NZS2033, AFC Drawings | Polyethylene Piping Installation Checklist | SUP | S | S |  |
|  | Gaskets and bolts installed and tensioned correctly. | AS/NZS2033 | AS/NZS2033, Client’s specs | Polyethylene Piping Installation Checklist | SUP | S | S |  |
|  | Pipe Pressure Test (Hydrostatic Test) |  |  |  |  |  |  |  |
|  | Verify that system for testing has been prepared for this activity (including placement of temporary items, dropping of all valves and instrument if installed). | PQMP | AS/NZS 2033, Approved Pipe Hydrostatic Test Procedure | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist | QR | I | I |  |
|  | Verify that pipe Hydrostatic Test is successfully done after it had achieved the approved acceptance criteria. | PQMP | AS/NZS 2033, Approved Pipe Hydrostatic Test Procedure | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist, pressure test records. | QR | H | H |  |
|  | Verify that piping is re-instated as per the Isometric drawing. | PQMP | AS/NZS 2033, Approved Pipe Hydrostatic Test Procedure | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist | QR | W | R | Can postpone this step if the temporary fittings are required for next activity |
|  | Pipe Flushing |  |  |  |  |  |  |  |
|  | Verify that the system has been prepared for this activity (including placement of temporary items) prior to introduction of pressurised flushing air or water. | PQMP | AS/NZS 2033, Approved Pipe Cleaning Procedure | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist | QR | W | R |  |
|  | For special services e.g. HP Steam, Chemicals, etc., ensure that medium for Pressure Test and Cleaning to be use (together with additional procedures & safety precautions) be approved by Client. | PQMP | AS/NZS 2033, Client’s specs | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist | QR | H | H |  |
|  | Verify that pipe cleaning is successfully done after it had achieved the approved acceptance criteria. | PQMP | AS/NZS 2033, Approved Pipe Cleaning Procedure | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist | QR | W | W |  |
|  | Verify that piping is re-instated as per the Isometric drawing. | PQMP | AS/NZS 2033, Approved Pipe Cleaning Procedure | Pipe Pressure, Cleaning, Drying & Leak Tests Checklist | QR | W | R | Can postpone this step if the temporary fittings are required for next activity |
|  | Other Pipe devices installation |  |  |  |  |  |  |  |
|  | Verify that all other pipeline devices e.g. cathodic protection system, insulations, earthing, lightning protection, etc. as required are correctly installed per manufacturer’s IOM. | PQMP | Device’s Manufacturer’s IOM, AFC drawings | Polyethylene Piping Installation Checklist | QR | R | R |  |
|  | Painting & Surface Treatment |  |  |  |  |  |  |  |
|  | Inspect and carry out Painting & Surface Treatment/touch up as required. | Client’s specs | Client’s specs | Coating & Surface Treatment Checklist | QR | W | R | Sub-contractor to supply detailed ITP |
|  | Mechanical Completion |  |  |  |  |  |  |  |
|  | Confirm complete compilation of all the Inspection & Test Records by discipline/system. This compilation will be added to the dossier for System/Area Mechanical Completion which when completed with all disciplines and other works will be submitted to Client for approval. | PQMP | Client’s specs | Compilation of Inspection & Test Records | QR | R | S |  |
|  | Quality Documents |  |  |  |  |  |  |  |
|  | Compilation of MDR | PQMP | Client’ Specs | MDR progressive review and sign off | QR | R | R |  |