## Register
INSPECTION AND TEST PLAN (ITP) REGISTER
|  | CLIENT : | Rio Tinto
|  | PROJECT : | Yandi Sustaining Project
|  | PROJECT No : | 1707
|  | SITE : | Yandicoogina Mine
|  | LAST UPDATED : | 2014-05-19
ITR No. | Title |  |  | Originator | Date Issued | Date Completed
ITP-001 | OFF SITE PIPING SUPPLY AND FABRICATION |  |  | Brian Zlnay | 2014-05-19 | XX/XX/XXXX
ITP-002 | OFF SITE STRUCTURAL SUPPLY AND FABRICATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-003 | DIESEL TANKS YTK605 & YTK606 SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-004 | OILY WATER SEPARATOR SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-005 | DIESEL PUMPS YPP734 A&B SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-006 | DIESEL PUMPS YPP12 & YPP40 SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-007 | DIESEL PUMPS YPP611 A&B SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-008 | DIESEL PUMPS YPP611 A&B SUPPLY AND INSTALLATION |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-009 | ON SITE STRUCTURAL INSTALLATION - JUNCTION SOUTH WEST |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-010 | ON SITE STRUCTURAL INSTALLATION - JUNCTION CENTRAL |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-011 | ON SITE PIPING INSTALLATION - JUNCTION SOUTH WEST |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-012 | ON SITE PIPING INSTALLATION - JUNCTION CENTRAL |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-013 | ELECTRICAL AND INSTRUMENTATION INSTALLATION JSW - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX
ITP-014 | ELECTRICAL AND INSTRUMENTATION INSTALLATION JC - ON SITE |  |  | Brian Zlnay | XX/XX/XXXX | XX/XX/XXXX

## ITP-001
ITP Number: |  | 01707-ITP-QA-001 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0003 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | B | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | PIPING SUPPLY AND FABRICATION – OFF SITE
Works Locations: |  | Fabrication Workshop
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | 2: Review Scope of Work and associated specifications; 3: I; 4: Client SOW: YSP-2963-SOW-M-001; 5: Not applicable; 6: Contract Document; 7: W
1.2 | 2013-11-11 | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Not applicable; 6: AFC Drawings, VDDI; 7: W
2 |  | 2: APPROVALS
2.1 | 2014-06-01 | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Not applicable; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
2.2 | 2014-06-01 | 2: Submit Weld Procedure Specifications & Qualifications; 3: I; 4: WPS & WPQ Reports; 5: ASME IX; AS1554;; 6: Approved WPSs; 7: W
2.3 | 2014-06-01 | 2: Submit Welder Qualifications; 3: I; 4: Welder Qualification Reports & register; 5: ASME IX; AS1554;; 6: Approved Welder Qualifications; 7: W
3 |  | 2: MATERIALS
3.1 | 2014-06-15 | 2: Monitor Incoming Materials (New) And Client supply; 3: I; 4: Client MTO; AFC Drawings; 01707-LST-ME-001; 5: YSP-0000-SPE-M-001 (Section 8,9); 6: Signed Delivery Dockets; Material Certificates, Inspection Certificates; 7: SV, W
3.2 | 2014-06-15 | 2: Material Traceability; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications; 5: Materials Specifications; 6: Traceability Records for Piping Works; 7: SV
4 |  | 2: MATERIALS PREPARATION
4.1 | 2014-06-17 | 2: Mark materials for cutting & weld preparation. Dimensional check.; 3: S; 4: Piping Isometrics & structural detail drawings; 5: AFC Drawings; 6: AFC Drawings, 01707-ITR-ME-008; 7: SV
4.2 | 2014-06-17 | 2: Prepare controlled/cut materials for fabrication; 3: S; 4: Material Control procedure, 01707-PLN-PM-002; 5: YSP-0000-SPE-M-001 (Section 2), AS4041; 6: AFC Drawings, 01707-ITR-ME-008; 7: SV
4.3 | 2014-06-17 | 2: Consumables Control; 3: S; 4: Consumable Control Procedure, 01707-PLN-PM-002; 5: YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1553; 6: Manufacturers Recommendations; 7: SV
5 |  | 2: FABRICATION
5.1 | 2014-06-17 | 2: Assemble material components as per drawing.; 3: S; 4: AFC Drawings; 5: YSP-0000-SPE-M-001 (Section 2), AS4041; 6: AFC Drawings; 7: SV
5.2 | 2014-06-17 | 2: Dimensional check & fit up inspection prior to welding; 3: S; 4: Dimensional check procedure, 01707-PLN-PM-002; 5: YSP-0000-SPE-M-001 (Section 2), AS4041; 6: AFC Drawings – isometric & fabrication detail drawings; 7: SV
5.3 | 2014-06-17 | 2: Welding of assembled components; 3: S; 4: Weld/Welder Traceability documentation:; 5: YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554; 6: Approved WPS’s; 01707-ITR-ME-008; 7: SV
5.4 | 2014-06-17 | 2: Ongoing visual weld inspection of all welded components.; 3: S; 4: Client Specifications, WPS; 5: YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554; 6: 01707-ITR-ME-008; 7: SV
6 |  | 2: INSPECTION & TESTING
6.1 | 2014-07-15 | 2: Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc; 3: I; 4: Dimensional check procedure, 01707-QA-PRO-003; 5: YSP-0000-SPE-M-001 (Section 2), AS4041; 6: AFC Drawings – isometric & fabrication detail drawings; 7: SV
6.2 | 2014-07-15 | 2: NDE in accordance with approved drawings, specifications; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001 (Section 2); 5: YSP-0000-SPE-M-001 (Section 2), AS4041; 6: Certified NATA reports;01707-ITR-ME-008; 7: SV
6.4 | 2014-07-15 | 2: Weld repairs; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001 (Section 2); 5: YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554; 6: Certified NATA reports;01707-ITR-ME-008; 7: H
6.5 | 2014-07-15 | 2: Hydrotest; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001 (Section 2); 5: YSP-0000-SPE-M-001 (Section 2), ASME IX, AS1554; 6: Certified NATA reports;01707-ITR-ME-008; 7: H
7 |  | 2: OFFSITE SURFACE TREATMENT
7.1 | 2014-07-20 | 2: Grit blast and prime; 3: S; 4: SS-P118_2 (Section 7); 5: SS-P118_2 (Section 7); 6: Surface Treatment Records; 7: SV
7.2 | 2014-07-20 | 2: Complete applicable surface treatment; 3: S; 4: SS-P118_2 (Section 9); 5: SS-P118_2 (Section 9); 6: Surface Treatment Records; 7: SV
8 |  | 2: ASSEMBLY & VERIFICATION
8.1 | 2014-07-25 | 2: Piping completion and verification; 3: S; 4: Construction Methodolgy (Schedule M of the Contract); 5: YSP-0000-SPE-M-001 (Section 8,9); 6: AFC Drawings & Specifications; 7: SV
8.2 | 2014-07-25 | 2: Punch listing completed; 3: S; 4: Construction Methodolgy (Schedule M of the Contract); 5: YSP-0000-SPE-M-001 (Section 8,9); 6: AFC Drawings, Punchlist & Specifications; 7: H
9 |  | 2: DESPATCH
9.1 | 2014-08-01 | 2: Review completed ITP; 3: I; 4: 01707-ITP-QA-001; 5: Not applicable; 6: Approved ITP; 7: SV, R
9.2 | 2014-08-01 | 2: Preparation & packaging for transport & load out to site; 3: I; 4: Inspection release form; 5: Primero Form; 6: Delivery Documentation; 7: W, H
9.4 | 2014-08-01 | 2: Delivery to Site; 3: I; 4: Inspection release – review & acceptance; 5: Primero Form; 6: Inspection Acceptance form; 7: W, H
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-002A
ITP Number: |  | #NAME? | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: | YSPA1034/A03/0003 | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | STRUCTURAL SUPPLY AND FABRICATION - OFF SITE
Works Locations: |  | Fabrication Workshop
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.1 | 2013-11-01 | 2: Review Scope of Work and associated specifications; 3: I; 4: Client SOW: YSP-2963-SOW-M-001; 5: Client Specifications, refer Note 1; 6: Contract Document; 7: W
1.2 | 2013-11-11 | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Client Specifications, refer Note 1; 6: AFC Drawings, VDDI; 7: W
2 |  | 2: APPROVALS
2.1 | 2014-02-01 | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Client Specifications, refer Note 1; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
2.2 | 2014-05-01 | 2: Submit Weld Procedure Specifications & Qualifications; 3: I; 4: WPS & WPQ Reports; 5: ASME IX; AS1554;; 6: Approved WPSs; 7: W
2.3 | 2014-05-01 | 2: Submit Welder Qualifications; 3: I; 4: Welder Qualification Reports & register; 5: ASME IX; AS1554;; 6: Approved Welder Qualifications; 7: W
3 |  | 2: MATERIALS
3.1 | 2014-05-01 | 2: Monitor Incoming Materials (New) And Client supply; 3: I; 4: Client MTO; AFC Drawings; 01707-LST-ME-001; 5: YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, refer Note 1; 6: Signed Delivery Dockets; Material Certificates, Inspection Certificates; 7: SV, W
3.2 | 2014-05-01 | 2: Material Traceability; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications; 5: Materials Specifications; 6: Traceability Records for Piping Works; 7: SV
4 |  | 2: MATERIALS PREPARATION
4.1 | 2014-05-01 | 2: Mark materials for cutting & weld preparation. Dimensional check.; 3: S; 4: Piping Isometrics & structural detail drawings; 5: AFC Drawings; 6: AFC Drawings, 01707-ITR-ME-008; 7: SV
4.2 | 2014-05-01 | 2: Prepare controlled/cut materials for fabrication; 3: S; 4: Material Control procedure, 01707-PLN-PM-002; 5: Client Specifications, refer Note 1; 6: AFC Drawings, 01707-ITR-ME-008; 7: SV
4.3 | 2014-05-01 | 2: Consumables Control; 3: S; 4: Consumable Control Procedure, 01707-PLN-PM-002; 5: Client Specifications, refer Note 1, and ASME IX, AS1554; 6: Manufacturers Recommendations; 7: SV
5 |  | 2: FABRICATION
5.1 | 2014-06-01 | 2: Assemble material components as per drawing.; 3: S; 4: AFC Drawings; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: AFC Drawings; 7: SV
5.2 | 2014-06-01 | 2: Dimensional check & fit up inspection prior to welding; 3: S; 4: Dimensional check procedure, 01707-PLN-PM-002; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: AFC Drawings – isometric & fabrication detail drawings; 7: SV
5.3 | 2014-06-01 | 2: Welding of assembled components; 3: S; 4: Weld/Welder Traceability documentation:; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: Approved WPS’s; 01707-ITR-ME-008; 7: SV
5.4 | 2014-06-01 | 2: Ongoing visual weld inspection of all welded components.; 3: S; 4: Client Specifications, WPS; 5: Client Specifications, refer Note 1, and AS 4041, AS 1554; 6: 01707-ITR-ME-008; 7: SV
6 |  | 2: INSPECTION & TESTING
6.1 | 2014-07-01 | 2: Perform final inspection after welding fabrication components: Visual, dimensional, distortion checks, etc; 3: I; 4: Dimensional check procedure, 01707-QA-PRO-003; 5: Client Specifications, refer Note 1; AS 4041; AS 1554;; 6: AFC Drawings – isometric & fabrication detail drawings; 7: SV
6.3 | 2014-07-01 | 2: Structural. NDE of lifting lugs in accordance with drawings/specifications (100%); 3: S; 4: NDE Procedures; YSP-0000-SPE-S-002; 5: Client Specifications, refer Note 1; AS 1554;; 6: Certified NATA reports;01707-ITR-ME-008; 7: SV
6.4 | 2014-07-01 | 2: Weld repairs; 3: S; 4: NDE Procedures; YSP-0000-SPE-M-001, YSP-0000-SPE-S-002; 5: Client Specifications, refer Note 1; AS 1554;; 6: Certified NATA reports;01707-ITR-ME-008; 7: H
7 |  | 2: OFFSITE SURFACE TREATMENT
7.1 | 2014-08-01 | 2: Grit blast and prime; 3: S; 5: Client Specifications, refer Note 1; 6: Surface Treatment Records; 7: SV
7.2 | 2014-08-01 | 2: Complete applicable surface treatment; 3: S; 5: Client Specifications, refer Note 1; 6: Surface Treatment Records; 7: SV
8 |  | 2: ASSEMBLY & VERIFICATION
8.1 | 2014-08-01 | 2: Structural completion and verification; 3: S; 4: Construction Methodolgy (Schedule M of the Contract); 5: Client Specifications, refer Note 1; 6: AFC Drawings & Specifications; 7: SV
8.2 | 2014-08-01 | 2: Punch listing completed; 3: S; 4: Construction Methodolgy (Schedule M of the Contract); 5: Client Specifications, refer Note 1; 6: AFC Drawings, Punchlist & Specifications; 7: H
9 |  | 2: DESPATCH
9.1 | 2014-09-01 | 2: Review completed ITP; 3: I; 4: 01707-ITP-QA--001; 5: Client Specifications, refer Note 1; 6: Approved ITP; 7: SV, R
9.2 | 2014-09-01 | 2: Preparation & packaging for transport & load out to site; 3: I; 4: Inspection release form; 5: Primero Form; 6: Delivery Documentation; 7: W, H
9.4 | 2014-09-01 | 2: Delivery to Site; 3: I; 4: Inspection release – review & acceptance; 5: Primero Form; 6: Inspection Acceptance form; 7: W, H
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-003A
ITP Number: |  | 01707-ITP-QA-002 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Structural, Mechanical and Piping Installation - ON-SITE JUNCTION SOUTH WEST
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.2 | 2014-08-01 | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Client Specifications, refer Note 1; 6: AFC Drawings, VDDI; 7: W
2 |  | 2: APPROVALS
2.1 | 2014-08-01 | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Client Specifications, refer Note 1; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
2.2 | 2014-08-01 | 2: Submit Weld Procedure Specifications & Qualifications; 3: I; 4: WPS & WPQ Reports; 5: ASME IX; AS1554;; 6: Approved WPSs; 7: W
2.3 | 2014-08-01 | 2: Submit Welder Qualifications; 3: I; 4: Welder Qualification Reports & register; 5: ASME IX; AS1554;; 6: Approved Welder Qualifications; 7: W
2.4 | 2014-08-01 | 2: Quality Plan, Inspection & Test Plan, NDT Procedures, NDE Operator Qualifications, Fabrication Procedures & Surface Treatment Procedures.; 3: I; 4: 01707-PLN-PM-002; 5: Client Specifications, refer Note 1; 6: Supplier Document Schedule (SDS) NDE Qualifications; 7: H/R
2.5 | 2014-08-01 | 2: Weld Procedure Specifications (WPS) and Weld Procedure Qualification Records (WPQR); 3: I; 4: 01707-PLN-PM-002; 5: AS 1554, AS 3992, AS 4041, YSP-0000-SPE-M-001, YSP-0000-S-002; 6: WPS & WPQR WPS Register; 7: H
2.6 | 2014-08-01 | 2: Welder Qualifications - Original test records available for review @ Primero Office. Qualify Welders in accordance with WPS; 3: I; 4: 01707-PLN-PM-002; 5: AS 1554, AS 3992, AS 4041, YSP-0000-SPE-M-001, YSP-0000-S-002; 6: Welder Qualification Record (WQR) Welder Qualification Register; 7: H
3 |  | 2: MATERIALS
3.1 | 2014-09-01 | 2: Inspect materials a per Material Control Procedure 01707-PRO-PM-017; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1. Data Sheets; 6: Delivery Dockets, Material Register & Certificates, Consumable Certificates, Data Sheets; 7: H
3.2 | 2014-09-01 | 2: Check for imperfections in flanges such as gouges and or protrusions in the serrations of gasket seating faces.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: YSP-0000-SPE-M-001; 6: Endorsed Material Certificates; 7: H/R
3.3 | 2014-09-01 | 2: Check the correct materials are installed in piping spools as specification and line class; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AS 4041, YSP-0000-SPE-M-001; 6: Endorsed Material Certificates; 7: H/R
3.4 | 2014-09-01 | 2: Store materials and welding consumables to eliminate damage and segregate Stainless Steel to prevent contamination.; 3: I; 4: Material Control Procedure; 5: Client Specifications, refer Note 1; 7: SV
3.5 | 2014-09-08 | 2: Check supply of vendor equipment for completeness; 3: I; 4: YSP-2963-SOW-M-001; 5: Visual Inspection; 6: Vendor Supply List & Delivery Docket; 7: W
4 | 2014-09-08 | 2: STRUCTURAL INSTALLATION; 3: I
4.1 | 2014-09-08 | 2: Anchor bolts and foundations checked (Location/ Elevation/ level); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings, YSP-0000-SPE-S-002; 6: Visual Inspection or Survey Report where required. Handover certificate from concrete contractor; 7: R
4.2 | 2014-09-08 | 2: Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Australian Standards and Regulations; 6: Certification Approved Lift Study Report where required; 7: H
4.3 | 2014-09-08 | 2: Erect Primary columns and beams following grid lines including vertical bracing.; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002, Approved Drawings; 6: 01707-ITR-ME-006 Survey Report; 7: H
4.4 | 2014-09-08 | 2: Structure Installed and checked (Location/ Elevation/ level) Snug tighten Primary connections throughout the structure Complete Primary steel pre-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002; 6: Visual Inspection or Survey Report where required
4.5 | 2014-09-08 | 2: Tension all primary steel bolts and nuts; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002, Approved Drawings; 6: 01707-ITR-ME-015; 7: W
4.6 | 2014-09-08 | 2: Complete primary steel post-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings; 6: Visual Inspection or Survey Report where required; 7: H
4.7 | 2014-09-08 | 2: Grouting; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002; 6: 01707-ITR-ME-014
4.8 | 2014-09-08 | 2: Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports Complete Secondary steel pre-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-006, Survey Report
4.9 | 2014-09-08 | 2: Tension all secondary steel bolts and nuts; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-015, Survey Report; 7: W
4.10 | 2014-09-08 | 2: Complete secondary steel post-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings; 6: Survey Report; 7: H
4.11 | 2014-09-08 | 2: Grating and handrails to be installed as required to ensure safe work practice and access.; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-006, Survey Report; 7: W
5 | 2014-09-08 | 2: MECHANICAL INSTALLATION; 3: I
5.1 | 2014-09-08 | 2: Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter and the entire grouting surface scabbled; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01707-ITR-ME-014, Survey Report; 7: H
5.2 | 2014-09-08 | 2: Check that the levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of mechanical equipment.; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01707-ITR-ME-011, Survey Report; 7: H
5.3 | 2014-09-08 | 2: Land equipment and confirm tie in points are within tolerance; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: Survey Reports
5.4 | 2014-09-08 | 2: Confirm piping tie-ins are complete and grout equipment. Check and verify grouting is acceptable; 3: I; 4: YSP-2963-SOW-M-001, Manufacturers directions; 5: AFC Drawings, Vendor IOM; 6: Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 or 01707-ITR-ME-014; 7: H
5.5 | 2014-09-08 | 2: Check alignment of drive/couplings Rotation Checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H & R
5.6 | 2014-09-08 | 2: Couplings Bolted, torqued and checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H
5.7 | 2014-09-08 | 2: V-Belts, or Chain drives installed and checked Safety guards installed and checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H
5.8 | 2014-09-08 | 2: Ensure no stress on nozzles from piping connection; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, cold spring check; 7: W
5.9 | 2014-09-08 | 2: Preservation & Maintenance; 3: I
5.10 | 2014-09-08 | 2: Ensure preservation and maintenance as per manufacturer recommendation; 3: I; 4: YSP-2963-SOW-M-001; 5: Vendor IOM; 6: Vendor IOM; 7: W
6 | 2014-09-08 | 2: PIPING
6.1 | 2014-09-08 | 2: Pre Processing and Assembly
6.1.1 | 2014-09-08 | 2: Material allocation, Transfer & marking of heat numbers. Mark piping material to required length. Cut pipe sections to length in readiness for Preparation, bevelling.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AFC Drawings; 6: Isometrics/Cutting List; 7: SV
6.1.2 | 2014-09-08 | 2: Assembly of components prior to welding. Check: Fit-up & alignment, Root Gap & Landing, Install pipe Supports as per Drawing.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 5: AFC Drawings, AS 4041, YSP-0000-M-001; 6: Isometrics/Cutting List; 7: H
6.1.3 | 2014-09-08 | 2: Dimensional check prior to welding.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 6: Isometrics/Cutting List; 7: H
6.1.4 | 2014-09-08 | 2: Welding (Field); 3: I; 4: AFC Drawings, YSP-0000-M-001
6.1.5 | 2014-09-08 | 2: Ensure Internals are clean and dry before welding.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-003; 7: SV
6.1.6 | 2014-09-08 | 2: Welding to be performed by qualified welder in accordance with approved welding Procedure Specification.; 3: I; 4: AFC Drawings, YSP-0000-M-001, WPS; 5: AS 4041, YSP-0000-M-001; 6: Welder Qualification Records Welder Register; 7: SV
6.1.7 | 2014-09-08 | 2: Carry out Welding of Joints , Field welds, Pipe supports & attachments.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: Visual Inspection; 7: H
6.1.8 | 2014-09-08 | 2: Welding visual Inspection, Check: Root pass/weld size/profile & finish Closing weld size/profile & finish Traceability records to be maintained, Welder, WPS Consumables etc.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-008, NDT Report; 7: SV
6.1.9 | 2014-09-08 | 2: Weld repairs (if any) remove defect and re-weld in accordance with qualified procedure.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-007, 01707-ITR-ME-008, NDT Report; 7: H
6.2 |  | 2: Inspection and Testing
6.2.1 | 2014-09-15 | 2: Dimensional check of piping assembly after welding "As Built"; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: As-Built Drawings; 7: H
6.2.2 | 2014-09-15 | 2: 100% Final visual inspection of all welds and traceability check.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-007, 'As Built' Drawings; 7: H
6.2.3 | 2014-09-15 | 2: Non Destructive Examination:; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.2.4 | 2014-09-15 | 2: Carry out required Non Destructive Examination (NDE) as per Client specification requirements. Extent of, as per applicable to the appropriate "AS4041 Class piping " and Piping line lists.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.3 |  | 2: Pipe Installation - Bolted Joints
6.3.1 | 2014-09-15 | 2: Inspect nozzle integrity on all static and rotating equipment to which pipe spools are connected.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001; 7: W
6.3.2 | 2014-09-15 | 2: Ensure Internals are clean and dry prior to assembly.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001; 7: H
6.3.3 | 2014-09-15 | 2: Shim steelwork at pipe support locations and survey for correct elevation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Visual Inspection or Survey results; 7: H/R
6.3.4 | 2014-09-15 | 2: Assembly - Install pipework Align mating flange joints to specified tolerances - To mechanical equipment. - To static equipment. - pipe to pipe.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics; 7: H
6.3.5 | 2014-09-15 | 2: Install in line piping components gaskets, nuts, bolts and Instrumentation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics, Material certificates; 7: H
6.3.6 | 2014-09-15 | 2: Check valves & instrumentation for Identification tags & check orientation. install valves and instrumentation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: P&ID's; 7: W
6.3.7 | 2014-09-15 | 2: Ensure correct bolts are installed & tensioned.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics, Torque Wrench Calibration Report; 7: R
6.4 |  | 2: Pressure Testing
6.4.1 | 2014-09-22 | 2: Develop Hydrostatic or Pneumatic Pressure Test Packs. Check NDE & Calibration Certificates prior to testing.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: System Test Pack; 7: H
6.4.2 | 2014-09-22 | 2: Flush clean piping system. The cleaning media shall be as per testing media detailed on the line List.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA Certified Pressure Test Report and Graph; 7: W
6.4.3 | 2014-09-22 | 2: Pressure Test Pipework 'Witness Test for any leaks'.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-005; 7: H
6.4.4 | 2014-09-22 | 2: Verification of cleanliness & dryness.; 3: I; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-005; 7: W
7 |  | 2: SURFACE TREATMENT (TOUCH UPS)
7.1 | 2014-09-22 | 2: Protect surfaces not requiring treatment, e.g. Field welds. nameplates. machined surfaces.; 3: S; 4: SS-P120, Client Specifications; 5: SS-P120; 6: Visual Inspection; 7: SV
7.2 | 2014-09-22 | 2: Check the blast medium is to the specifications.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.3 | 2014-09-22 | 2: Check surface cleaning as per specification; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.4 | 2014-09-22 | 2: Monitor atmospheric conditions daily for Temperature (> 5 •c and <50 •c) and Humidity (>20% and <85%); 3: S; 5: SS-P120; 6: Visual Inspection or Bureau of Meteorology Data; 7: SV
7.5 | 2014-09-22 | 2: Check item to be painted (piping I steelwork etc.) for defects, damage. No welding flux, splatter, sharp edges etc. Confirm all inspections, NOT etc. on the item have been completed prior to painting.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: H
7.6 | 2014-09-22 | 2: Ensure the items to be painted are adequately laid out and masked as needed; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.7 | 2014-09-22 | 2: Check correct paint is being used; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions, AFC drawings; 5: SS-P120; 6: Visual Inspection; 7: SV
7.8 | 2014-09-22 | 2: Ensure paints are mixed as per manufacturers recommendation; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.9 | 2014-09-22 | 2: Check application is correct and is free of paint runs and other defects; 3: I; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: DFT report; 7: SV
8 |  | 2: FINAL INSPECTION ON COMPLETION
8.1 | 2014-09-25 | 2: -Carry out final inspection -Generate punch list -Verification / clearance of punch list; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Field Inspection Checklist (FIC) 's Completions database; 7: H
9 |  | 2: FINALISE DOCUMENTATION
9.1 | 2014-09-25 | 2: Progressively check all test reports are correct.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Reviewed and Approved ITR's; 7: H
9.2 | 2014-09-25 | 2: Sign off Inspection & Test Plan.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: ITP; 7: R
9.3 | 2014-09-25 | 2: MDR to be progressively compiled and submitted to client for final approval.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: MDR; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-022
ITP Number: |  | 01707-ITP-QA-003 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Structural, Mechanical and Piping Installation - ON-SITE JUNCTION CENTRAL
Works Locations: |  | JC
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.2 | 2014-08-01 | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Client Specifications, refer Note 1; 6: AFC Drawings, VDDI; 7: W
2 |  | 2: APPROVALS
2.1 | 2014-08-01 | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Client Specifications, refer Note 1; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
2.2 | 2014-08-01 | 2: Submit Weld Procedure Specifications & Qualifications; 3: I; 4: WPS & WPQ Reports; 5: ASME IX; AS1554;; 6: Approved WPSs; 7: W
2.3 | 2014-08-01 | 2: Submit Welder Qualifications; 3: I; 4: Welder Qualification Reports & register; 5: ASME IX; AS1554;; 6: Approved Welder Qualifications; 7: W
2.4 | 2014-08-01 | 2: Quality Plan, Inspection & Test Plan, NDT Procedures, NDE Operator Qualifications, Fabrication Procedures & Surface Treatment Procedures.; 3: I; 4: 01707-PLN-PM-002; 5: Client Specifications, refer Note 1; 6: Supplier Document Schedule (SDS) NDE Qualifications; 7: H/R
2.5 | 2014-08-01 | 2: Weld Procedure Specifications (WPS) and Weld Procedure Qualification Records (WPQR); 3: I; 4: 01707-PLN-PM-002; 5: AS 1554, AS 3992, AS 4041, YSP-0000-SPE-M-001, YSP-0000-S-002; 6: WPS & WPQR WPS Register; 7: H
2.6 | 2014-08-01 | 2: Welder Qualifications - Original test records available for review @ Primero Office. Qualify Welders in accordance with WPS; 3: I; 4: 01707-PLN-PM-002; 5: AS 1554, AS 3992, AS 4041, YSP-0000-SPE-M-001, YSP-0000-S-002; 6: Welder Qualification Record (WQR) Welder Qualification Register; 7: H
3 |  | 2: MATERIALS
3.1 | 2014-09-01 | 2: Inspect materials a per Material Control Procedure 01707-PRO-PM-017; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1. Data Sheets; 6: Delivery Dockets, Material Register & Certificates, Consumable Certificates, Data Sheets; 7: H
3.2 | 2014-09-01 | 2: Check for imperfections in flanges such as gouges and or protrusions in the serrations of gasket seating faces.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: YSP-0000-SPE-M-001; 6: Endorsed Material Certificates; 7: H/R
3.3 | 2014-09-01 | 2: Check the correct materials are installed in piping spools as specification and line class; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AS 4041, YSP-0000-SPE-M-001; 6: Endorsed Material Certificates; 7: H/R
3.4 | 2014-09-01 | 2: Store materials and welding consumables to eliminate damage and segregate Stainless Steel to prevent contamination.; 3: I; 4: Material Control Procedure; 5: Client Specifications, refer Note 1; 7: SV
3.5 | 2014-09-08 | 2: Check supply of vendor equipment for completeness; 3: I; 4: YSP-2963-SOW-M-001; 5: Visual Inspection; 6: Vendor Supply List & Delivery Docket; 7: W
4 | 2014-09-08 | 2: STRUCTURAL INSTALLATION; 3: I
4.1 | 2014-09-08 | 2: Anchor bolts and foundations checked (Location/ Elevation/ level); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings, YSP-0000-SPE-S-002; 6: Visual Inspection or Survey Report where required. Handover certificate from concrete contractor; 7: R
4.2 | 2014-09-08 | 2: Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Australian Standards and Regulations; 6: Certification Approved Lift Study Report where required; 7: H
4.3 | 2014-09-08 | 2: Erect Primary columns and beams following grid lines including vertical bracing.; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002, Approved Drawings; 6: 01707-ITR-ME-006 Survey Report; 7: H
4.4 | 2014-09-08 | 2: Structure Installed and checked (Location/ Elevation/ level) Snug tighten Primary connections throughout the structure Complete Primary steel pre-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002; 6: Visual Inspection or Survey Report where required
4.5 | 2014-09-08 | 2: Tension all primary steel bolts and nuts; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002, Approved Drawings; 6: 01707-ITR-ME-015; 7: W
4.6 | 2014-09-08 | 2: Complete primary steel post-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings; 6: Visual Inspection or Survey Report where required; 7: H
4.7 | 2014-09-08 | 2: Grouting; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002; 6: 01707-ITR-ME-014
4.8 | 2014-09-08 | 2: Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports Complete Secondary steel pre-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-006, Survey Report
4.9 | 2014-09-08 | 2: Tension all secondary steel bolts and nuts; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-015, Survey Report; 7: W
4.10 | 2014-09-08 | 2: Complete secondary steel post-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings; 6: Survey Report; 7: H
4.11 | 2014-09-08 | 2: Grating and handrails to be installed as required to ensure safe work practice and access.; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-006, Survey Report; 7: W
5 | 2014-09-08 | 2: MECHANICAL INSTALLATION; 3: I
5.1 | 2014-09-08 | 2: Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter and the entire grouting surface scabbled; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01707-ITR-ME-014, Survey Report; 7: H
5.2 | 2014-09-08 | 2: Check that the levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of mechanical equipment.; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01707-ITR-ME-011, Survey Report; 7: H
5.3 | 2014-09-08 | 2: Land equipment and confirm tie in points are within tolerance; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: Survey Reports
5.4 | 2014-09-08 | 2: Confirm piping tie-ins are complete and grout equipment. Check and verify grouting is acceptable; 3: I; 4: YSP-2963-SOW-M-001, Manufacturers directions; 5: AFC Drawings, Vendor IOM; 6: Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 or 01707-ITR-ME-014; 7: H
5.5 | 2014-09-08 | 2: Check alignment of drive/couplings Rotation Checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H & R
5.6 | 2014-09-08 | 2: Couplings Bolted, torqued and checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H
5.7 | 2014-09-08 | 2: V-Belts, or Chain drives installed and checked Safety guards installed and checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H
5.8 | 2014-09-08 | 2: Ensure no stress on nozzles from piping connection; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, cold spring check; 7: W
5.9 | 2014-09-08 | 2: Preservation & Maintenance; 3: I
5.10 | 2014-09-08 | 2: Ensure preservation and maintenance as per manufacturer recommendation; 3: I; 4: YSP-2963-SOW-M-001; 5: Vendor IOM; 6: Vendor IOM; 7: W
6 | 2014-09-08 | 2: PIPING
6.1 | 2014-09-08 | 2: Pre Processing and Assembly
6.1.1 | 2014-09-08 | 2: Material allocation, Transfer & marking of heat numbers. Mark piping material to required length. Cut pipe sections to length in readiness for Preparation, bevelling.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AFC Drawings; 6: Isometrics/Cutting List; 7: SV
6.1.2 | 2014-09-08 | 2: Assembly of components prior to welding. Check: Fit-up & alignment, Root Gap & Landing, Install pipe Supports as per Drawing.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 5: AFC Drawings, AS 4041, YSP-0000-M-001; 6: Isometrics/Cutting List; 7: H
6.1.3 | 2014-09-08 | 2: Dimensional check prior to welding.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 6: Isometrics/Cutting List; 7: H
6.1.4 | 2014-09-08 | 2: Welding (Field); 3: I; 4: AFC Drawings, YSP-0000-M-001
6.1.5 | 2014-09-08 | 2: Ensure Internals are clean and dry before welding.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-003; 7: SV
6.1.6 | 2014-09-08 | 2: Welding to be performed by qualified welder in accordance with approved welding Procedure Specification.; 3: I; 4: AFC Drawings, YSP-0000-M-001, WPS; 5: AS 4041, YSP-0000-M-001; 6: Welder Qualification Records Welder Register; 7: SV
6.1.7 | 2014-09-08 | 2: Carry out Welding of Joints , Field welds, Pipe supports & attachments.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: Visual Inspection; 7: H
6.1.8 | 2014-09-08 | 2: Welding visual Inspection, Check: Root pass/weld size/profile & finish Closing weld size/profile & finish Traceability records to be maintained, Welder, WPS Consumables etc.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-008, NDT Report; 7: SV
6.1.9 | 2014-09-08 | 2: Weld repairs (if any) remove defect and re-weld in accordance with qualified procedure.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-007, 01707-ITR-ME-008, NDT Report; 7: H
6.2 |  | 2: Inspection and Testing
6.2.1 | 2014-09-15 | 2: Dimensional check of piping assembly after welding "As Built"; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: As-Built Drawings; 7: H
6.2.2 | 2014-09-15 | 2: 100% Final visual inspection of all welds and traceability check.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-007, 'As Built' Drawings; 7: H
6.2.3 | 2014-09-15 | 2: Non Destructive Examination:; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.2.4 | 2014-09-15 | 2: Carry out required Non Destructive Examination (NDE) as per Client specification requirements. Extent of, as per applicable to the appropriate "AS4041 Class piping " and Piping line lists.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.3 |  | 2: Pipe Installation - Bolted Joints
6.3.1 | 2014-09-15 | 2: Inspect nozzle integrity on all static and rotating equipment to which pipe spools are connected.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001; 7: W
6.3.2 | 2014-09-15 | 2: Ensure Internals are clean and dry prior to assembly.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001; 7: H
6.3.3 | 2014-09-15 | 2: Shim steelwork at pipe support locations and survey for correct elevation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Visual Inspection or Survey results; 7: H/R
6.3.4 | 2014-09-15 | 2: Assembly - Install pipework Align mating flange joints to specified tolerances - To mechanical equipment. - To static equipment. - pipe to pipe.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics; 7: H
6.3.5 | 2014-09-15 | 2: Install in line piping components gaskets, nuts, bolts and Instrumentation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics, Material certificates; 7: H
6.3.6 | 2014-09-15 | 2: Check valves & instrumentation for Identification tags & check orientation. install valves and instrumentation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: P&ID's; 7: W
6.3.7 | 2014-09-15 | 2: Ensure correct bolts are installed & tensioned.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics, Torque Wrench Calibration Report; 7: R
6.4 |  | 2: Pressure Testing
6.4.1 | 2014-09-22 | 2: Develop Hydrostatic or Pneumatic Pressure Test Packs. Check NDE & Calibration Certificates prior to testing.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: System Test Pack; 7: H
6.4.2 | 2014-09-22 | 2: Flush clean piping system. The cleaning media shall be as per testing media detailed on the line List.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA Certified Pressure Test Report and Graph; 7: W
6.4.3 | 2014-09-22 | 2: Pressure Test Pipework 'Witness Test for any leaks'.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-005; 7: H
6.4.4 | 2014-09-22 | 2: Verification of cleanliness & dryness.; 3: I; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-005; 7: W
7 |  | 2: SURFACE TREATMENT (TOUCH UPS)
7.1 | 2014-09-22 | 2: Protect surfaces not requiring treatment, e.g. Field welds. nameplates. machined surfaces.; 3: S; 4: SS-P120, Client Specifications; 5: SS-P120; 6: Visual Inspection; 7: SV
7.2 | 2014-09-22 | 2: Check the blast medium is to the specifications.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.3 | 2014-09-22 | 2: Check surface cleaning as per specification; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.4 | 2014-09-22 | 2: Monitor atmospheric conditions daily for Temperature (> 5 •c and <50 •c) and Humidity (>20% and <85%); 3: S; 5: SS-P120; 6: Visual Inspection or Bureau of Meteorology Data; 7: SV
7.5 | 2014-09-22 | 2: Check item to be painted (piping I steelwork etc.) for defects, damage. No welding flux, splatter, sharp edges etc. Confirm all inspections, NOT etc. on the item have been completed prior to painting.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: H
7.6 | 2014-09-22 | 2: Ensure the items to be painted are adequately laid out and masked as needed; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.7 | 2014-09-22 | 2: Check correct paint is being used; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions, AFC drawings; 5: SS-P120; 6: Visual Inspection; 7: SV
7.8 | 2014-09-22 | 2: Ensure paints are mixed as per manufacturers recommendation; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.9 | 2014-09-22 | 2: Check application is correct and is free of paint runs and other defects; 3: I; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: DFT report; 7: SV
8 |  | 2: FINAL INSPECTION ON COMPLETION
8.1 | 2014-09-25 | 2: -Carry out final inspection -Generate punch list -Verification / clearance of punch list; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Field Inspection Checklist (FIC) 's Completions database; 7: H
9 |  | 2: FINALISE DOCUMENTATION
9.1 | 2014-09-25 | 2: Progressively check all test reports are correct.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Reviewed and Approved ITR's; 7: H
9.2 | 2014-09-25 | 2: Sign off Inspection & Test Plan.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: ITP; 7: R
9.3 | 2014-09-25 | 2: MDR to be progressively compiled and submitted to client for final approval.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: MDR; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-0222
ITP Number: |  | 01707-ITP-QA-004 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Electrical & Instrumentation Supply and Installation - ON-SITE JUNCTION SOUTH WEST
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | 2014-08-01 | 2: Site Preparation, Planning and Inspection; 3: I; 4: 01707-SWI-HS-093 Site Preparation, Planning and Inspection; 5: 01707-SWI-HS-093 Site Preparation, Planning and Inspection; 6: N/A
2 | 2014-09-01 | 2: Installation of Cable Ladders and Trays; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-091 Installation of Cable Tray and Cable Ladder 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-091 Installation of Cable Tray and Cable Ladder 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01707-ITR-EL-033 Cable Tray - Ladder; 7: R
3 | 2014-09-02 | 2: Installation of Below Ground Conduits; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-094 Trenching, Excavating, Pot Holing 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-094 Trenching, Excavating, Pot Holing 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01707-ITR-EL-036 Underground Cable Installation; 7: W, R
4 | 2014-09-03 | 2: Installation of Aboveground Rigid Discontinuous Conduit; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01707-ITR-EL-034 Above Ground Conduit; 7: R
5 | 2014-09-04 | 2: Installation of Cables and Fibre Optic Cables; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-092 Installation of Cables 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-092 Installation of Cables 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-001 On Drum Testing for Cables 01707-ITR-EL-002 Cable Installation 01707-ITR-EL-036 Underground Cable Installation; 7: W, R
6 | 2014-09-05 | 2: Installation of Electrical Earthing; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-015 Electrical Earthing; 7: W, R
7 | 2014-09-06 | 2: Installation of Kiosk; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-011 Distribution Board Installation; 7: R
8 | 2014-09-07 | 2: Testing and Termination Cables; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-003 Cable Test 01707-ITR-EL-004 Cable Termination; 7: R
9 | 2014-09-08 | 2: Installation of Local Control Stations; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-030 Local Control; 7: R
10 | 2014-09-09 | 2: Installation of Lighting and lighting Poles; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-029 Lighting; 7: R
11 | 2014-09-10 | 2: Installation of Control Panels; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-023 Control Panel; 7: R
12 | 2014-09-11 | 2: Installation of Equipment Pre Installation; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-003 Equipment Pre-Installation Verification; 7: R
13 | 2014-09-12 | 2: Installation of Instruments; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-001 Instrument Installation 01707-ITR-IN-003 Equipment Pre-Installation Verification; 7: R
14 | 2014-09-13 | 2: Installation of Instrument Tubing; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-006 Instrument Tubing Installation; 7: R
15 | 2014-09-14 | 2: Installation of Pressure Safety Valves; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-002 Pressure Relief Valve Preinstallation; 7: W, R
16 | 2014-09-15 | 2: Instrument Loop Checks; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-007 Instrument Loop Check; 7: R
17 | 2014-09-16 | 2: Installation of Electrical Motors; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-017 Electrical Motor Installation; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-02222
ITP Number: |  | 01707-ITP-QA-005 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Electrical & Instrumentation Supply and Installation - ON-SITE JUNCTION CENTRAL
Works Locations: |  | JC
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | 2014-08-01 | 2: Site Preparation, Planning and Inspection; 3: I; 4: 01707-SWI-HS-093 Site Preparation, Planning and Inspection; 5: 01707-SWI-HS-093 Site Preparation, Planning and Inspection; 6: N/A
2 | 2014-09-01 | 2: Installation of Cable Ladders and Trays; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-091 Installation of Cable Tray and Cable Ladder 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-091 Installation of Cable Tray and Cable Ladder 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01707-ITR-EL-033 Cable Tray - Ladder; 7: R
3 | 2014-09-02 | 2: Installation of Below Ground Conduits; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-094 Trenching, Excavating, Pot Holing 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-094 Trenching, Excavating, Pot Holing 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01707-ITR-EL-036 Underground Cable Installation; 7: W, R
4 | 2014-09-03 | 2: Installation of Aboveground Rigid Discontinuous Conduit; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure; 6: 01707-ITR-EL-034 Above Ground Conduit; 7: R
5 | 2014-09-04 | 2: Installation of Cables and Fibre Optic Cables; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-092 Installation of Cables 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-SWI-HS-092 Installation of Cables 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-001 On Drum Testing for Cables 01707-ITR-EL-002 Cable Installation 01707-ITR-EL-036 Underground Cable Installation; 7: W, R
6 | 2014-09-05 | 2: Installation of Electrical Earthing; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-015 Electrical Earthing; 7: W, R
7 | 2014-09-06 | 2: Installation of Kiosk; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-011 Distribution Board Installation; 7: R
8 | 2014-09-07 | 2: Testing and Termination Cables; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-003 Cable Test 01707-ITR-EL-004 Cable Termination; 7: R
9 | 2014-09-08 | 2: Installation of Local Control Stations; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-030 Local Control; 7: R
10 | 2014-09-09 | 2: Installation of Lighting and lighting Poles; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-029 Lighting; 7: R
11 | 2014-09-10 | 2: Installation of Control Panels; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-023 Control Panel; 7: R
12 | 2014-09-11 | 2: Installation of Equipment Pre Installation; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-003 Equipment Pre-Installation Verification; 7: R
13 | 2014-09-12 | 2: Installation of Instruments; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-001 Instrument Installation 01707-ITR-IN-003 Equipment Pre-Installation Verification; 7: R
14 | 2014-09-13 | 2: Installation of Instrument Tubing; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-006 Instrument Tubing Installation; 7: R
15 | 2014-09-14 | 2: Installation of Pressure Safety Valves; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-002 Pressure Relief Valve Preinstallation; 7: W, R
16 | 2014-09-15 | 2: Instrument Loop Checks; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-IN-007 Instrument Loop Check; 7: R
17 | 2014-09-16 | 2: Installation of Electrical Motors; 3: I; 4: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 5: 01707-PRO-EL-005 Inspection Test Record Procedure 01707-PRO-EL-004_A Electrical ITR Matrix Procedure 01707-PRO-EL-002_A Electrical Testing and Reporting Procedure 01707-PRO-EL-007 Calibration and Equipment Procedure; 6: 01707-ITR-EL-017 Electrical Motor Installation; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;

## ITP-002 (2)
ITP Number: |  | 01707-ITP-QA-002 | Client Contract Number: | YSP/A/CC/1034 | Contract Item Number: |  | Legend: | W = Witness | S = Subcontractor |  | I = In House
Revision Number: |  | A | Contractor Approval: |  | Equipment Number: |  |  | H = Hold | SV = Surveillance |  | R = Review
Contractor: |  | Primero Group | Description of Service: | Structural, Mechanical and Piping Installation - ON-SITE JUNCTION SOUTH WEST
Works Locations: |  | JSW
Task Number | Probable Date | Task Description | Location Code (I or S) | Controlling Procedure or Instruction | Acceptance Criteria | Verifying Documents | Inspection Requirements |  |  |  |  | Contractor Signature
[7 empty] | Contractor | Engineer |  |  | Client
[8 empty] | Insp | Engineer | Signature
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 |  | 2: DESIGN/SPECIFICATIONS
1.2 | 2014-08-01 | 2: Review Drawings & Data Sheets; 3: I; 4: AFC Drawings & Data Sheets; 5: Client Specifications, refer Note 1; 6: AFC Drawings, VDDI; 7: W
2 |  | 2: APPROVALS
2.1 | 2014-08-01 | 2: Submit Project Documentation, ITP, NDE procedures, Pressure testing procedures; 3: I; 4: ITP, NDE procedures, Pressure testing procedures; 5: Client Specifications, refer Note 1; 6: Approved ITP’s NDE procedures, Pressure testing procedures; 7: W, H
2.2 | 2014-08-01 | 2: Submit Weld Procedure Specifications & Qualifications; 3: I; 4: WPS & WPQ Reports; 5: ASME IX; AS1554;; 6: Approved WPSs; 7: W
2.3 | 2014-08-01 | 2: Submit Welder Qualifications; 3: I; 4: Welder Qualification Reports & register; 5: ASME IX; AS1554;; 6: Approved Welder Qualifications; 7: W
2.4 | 2014-08-01 | 2: Quality Plan, Inspection & Test Plan, NDT Procedures, NDE Operator Qualifications, Fabrication Procedures & Surface Treatment Procedures.; 3: I; 4: 01707-PLN-PM-002; 5: Client Specifications, refer Note 1; 6: Supplier Document Schedule (SDS) NDE Qualifications; 7: H/R
2.5 | 2014-08-01 | 2: Weld Procedure Specifications (WPS) and Weld Procedure Qualification Records (WPQR); 3: I; 4: 01707-PLN-PM-002; 5: AS 1554, AS 3992, AS 4041, YSP-0000-SPE-M-001, YSP-0000-S-002; 6: WPS & WPQR WPS Register; 7: H
2.6 | 2014-08-01 | 2: Welder Qualifications - Original test records available for review @ Primero Office. Qualify Welders in accordance with WPS; 3: I; 4: 01707-PLN-PM-002; 5: AS 1554, AS 3992, AS 4041, YSP-0000-SPE-M-001, YSP-0000-S-002; 6: Welder Qualification Record (WQR) Welder Qualification Register; 7: H
3 |  | 2: MATERIALS
3.1 | 2014-09-01 | 2: Inspect materials a per Material Control Procedure 01707-PRO-PM-017; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1. Data Sheets; 6: Delivery Dockets, Material Register & Certificates, Consumable Certificates, Data Sheets; 7: H
3.2 | 2014-09-01 | 2: Check for imperfections in flanges such as gouges and or protrusions in the serrations of gasket seating faces.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: YSP-0000-SPE-M-001; 6: Endorsed Material Certificates; 7: H/R
3.3 | 2014-09-01 | 2: Check the correct materials are installed in piping spools as specification and line class; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AS 4041, YSP-0000-SPE-M-001; 6: Endorsed Material Certificates; 7: H/R
3.4 | 2014-09-01 | 2: Store materials and welding consumables to eliminate damage and segregate Stainless Steel to prevent contamination.; 3: I; 4: Material Control Procedure; 5: Client Specifications, refer Note 1; 7: SV
3.5 | 2014-09-08 | 2: Check supply of vendor equipment for completeness; 3: I; 4: YSP-2963-SOW-M-001; 5: Visual Inspection; 6: Vendor Supply List & Delivery Docket; 7: W
4 | 2014-09-08 | 2: STRUCTURAL INSTALLATION; 3: I
4.1 | 2014-09-08 | 2: Anchor bolts and foundations checked (Location/ Elevation/ level); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings, YSP-0000-SPE-S-002; 6: Visual Inspection or Survey Report where required. Handover certificate from concrete contractor; 7: R
4.2 | 2014-09-08 | 2: Verify spreader bars and appropriate Lifting/Rigging equipment is available Lift Study to be completed and approved (as required); 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Australian Standards and Regulations; 6: Certification Approved Lift Study Report where required; 7: H
4.3 | 2014-09-08 | 2: Erect Primary columns and beams following grid lines including vertical bracing.; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002, Approved Drawings; 6: 01707-ITR-ME-006 Survey Report; 7: H
4.4 | 2014-09-08 | 2: Structure Installed and checked (Location/ Elevation/ level) Snug tighten Primary connections throughout the structure Complete Primary steel pre-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002; 6: Visual Inspection or Survey Report where required
4.5 | 2014-09-08 | 2: Tension all primary steel bolts and nuts; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002, Approved Drawings; 6: 01707-ITR-ME-015; 7: W
4.6 | 2014-09-08 | 2: Complete primary steel post-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings; 6: Visual Inspection or Survey Report where required; 7: H
4.7 | 2014-09-08 | 2: Grouting; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100, YSP-0000-S-002; 6: 01707-ITR-ME-014
4.8 | 2014-09-08 | 2: Install Secondary steel i.e.. - Floor support steel work - Horizontal bracing - Pipe and cable tray supports Complete Secondary steel pre-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-006, Survey Report
4.9 | 2014-09-08 | 2: Tension all secondary steel bolts and nuts; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-015, Survey Report; 7: W
4.10 | 2014-09-08 | 2: Complete secondary steel post-tension survey; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: Approved Drawings; 6: Survey Report; 7: H
4.11 | 2014-09-08 | 2: Grating and handrails to be installed as required to ensure safe work practice and access.; 3: I; 4: Construction Methodology (Schedule M of the Contract); 5: AS 4100 Approved Drawings; 6: 01707-ITR-ME-006, Survey Report; 7: W
5 | 2014-09-08 | 2: MECHANICAL INSTALLATION; 3: I
5.1 | 2014-09-08 | 2: Verify foundations & bolt locations. Foundations shall be free from oil or foreign matter and the entire grouting surface scabbled; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01707-ITR-ME-014, Survey Report; 7: H
5.2 | 2014-09-08 | 2: Check that the levels and alignments are set out within tolerance. Foundation bolt, nut & washers to be set and surveyed prior to landing of mechanical equipment.; 3: I; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: 01707-ITR-ME-011, Survey Report; 7: H
5.3 | 2014-09-08 | 2: Land equipment and confirm tie in points are within tolerance; 4: Vendor IOM, Scope of Work; 5: AFC Drawings, Vendor IOM; 6: Survey Reports
5.4 | 2014-09-08 | 2: Confirm piping tie-ins are complete and grout equipment. Check and verify grouting is acceptable; 3: I; 4: YSP-2963-SOW-M-001, Manufacturers directions; 5: AFC Drawings, Vendor IOM; 6: Material Safety Data Sheets (MSDS), 01707-ITR-ME-013 or 01707-ITR-ME-014; 7: H
5.5 | 2014-09-08 | 2: Check alignment of drive/couplings Rotation Checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H & R
5.6 | 2014-09-08 | 2: Couplings Bolted, torqued and checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H
5.7 | 2014-09-08 | 2: V-Belts, or Chain drives installed and checked Safety guards installed and checked; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, Vendor IOM; 7: H
5.8 | 2014-09-08 | 2: Ensure no stress on nozzles from piping connection; 3: I; 4: YSP-2963-SOW-M-001, SS-M101; 5: AFC Drawings, SS-M101, Vendor IOM; 6: 01707-ITR-ME-011, cold spring check; 7: W
5.9 | 2014-09-08 | 2: Preservation & Maintenance; 3: I
5.10 | 2014-09-08 | 2: Ensure preservation and maintenance as per manufacturer recommendation; 3: I; 4: YSP-2963-SOW-M-001; 5: Vendor IOM; 6: Vendor IOM; 7: W
6 | 2014-09-08 | 2: PIPING
6.1 | 2014-09-08 | 2: Pre Processing and Assembly
6.1.1 | 2014-09-08 | 2: Material allocation, Transfer & marking of heat numbers. Mark piping material to required length. Cut pipe sections to length in readiness for Preparation, bevelling.; 3: I; 4: AFC Drawings, Material Control Procedure, and Client Specifications, refer Note 1; 5: AFC Drawings; 6: Isometrics/Cutting List; 7: SV
6.1.2 | 2014-09-08 | 2: Assembly of components prior to welding. Check: Fit-up & alignment, Root Gap & Landing, Install pipe Supports as per Drawing.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 5: AFC Drawings, AS 4041, YSP-0000-M-001; 6: Isometrics/Cutting List; 7: H
6.1.3 | 2014-09-08 | 2: Dimensional check prior to welding.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 6: Isometrics/Cutting List; 7: H
6.1.4 | 2014-09-08 | 2: Welding (Field); 3: I; 4: AFC Drawings, YSP-0000-M-001
6.1.5 | 2014-09-08 | 2: Ensure Internals are clean and dry before welding.; 3: I; 4: AFC Drawings, YSP-0000-M-001; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-003; 7: SV
6.1.6 | 2014-09-08 | 2: Welding to be performed by qualified welder in accordance with approved welding Procedure Specification.; 3: I; 4: AFC Drawings, YSP-0000-M-001, WPS; 5: AS 4041, YSP-0000-M-001; 6: Welder Qualification Records Welder Register; 7: SV
6.1.7 | 2014-09-08 | 2: Carry out Welding of Joints , Field welds, Pipe supports & attachments.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: Visual Inspection; 7: H
6.1.8 | 2014-09-08 | 2: Welding visual Inspection, Check: Root pass/weld size/profile & finish Closing weld size/profile & finish Traceability records to be maintained, Welder, WPS Consumables etc.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-008, NDT Report; 7: SV
6.1.9 | 2014-09-08 | 2: Weld repairs (if any) remove defect and re-weld in accordance with qualified procedure.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-007, 01707-ITR-ME-008, NDT Report; 7: H
6.2 |  | 2: Inspection and Testing
6.2.1 | 2014-09-15 | 2: Dimensional check of piping assembly after welding "As Built"; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: As-Built Drawings; 7: H
6.2.2 | 2014-09-15 | 2: 100% Final visual inspection of all welds and traceability check.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-007, 'As Built' Drawings; 7: H
6.2.3 | 2014-09-15 | 2: Non Destructive Examination:; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.2.4 | 2014-09-15 | 2: Carry out required Non Destructive Examination (NDE) as per Client specification requirements. Extent of, as per applicable to the appropriate "AS4041 Class piping " and Piping line lists.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA endorsed Non Destructive Examination Reports; 7: H
6.3 |  | 2: Pipe Installation - Bolted Joints
6.3.1 | 2014-09-15 | 2: Inspect nozzle integrity on all static and rotating equipment to which pipe spools are connected.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001; 7: W
6.3.2 | 2014-09-15 | 2: Ensure Internals are clean and dry prior to assembly.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001; 7: H
6.3.3 | 2014-09-15 | 2: Shim steelwork at pipe support locations and survey for correct elevation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Visual Inspection or Survey results; 7: H/R
6.3.4 | 2014-09-15 | 2: Assembly - Install pipework Align mating flange joints to specified tolerances - To mechanical equipment. - To static equipment. - pipe to pipe.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics; 7: H
6.3.5 | 2014-09-15 | 2: Install in line piping components gaskets, nuts, bolts and Instrumentation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics, Material certificates; 7: H
6.3.6 | 2014-09-15 | 2: Check valves & instrumentation for Identification tags & check orientation. install valves and instrumentation.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: P&ID's; 7: W
6.3.7 | 2014-09-15 | 2: Ensure correct bolts are installed & tensioned.; 3: I; 4: AFC Drawings, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-001, Isometrics, Torque Wrench Calibration Report; 7: R
6.4 |  | 2: Pressure Testing
6.4.1 | 2014-09-22 | 2: Develop Hydrostatic or Pneumatic Pressure Test Packs. Check NDE & Calibration Certificates prior to testing.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: System Test Pack; 7: H
6.4.2 | 2014-09-22 | 2: Flush clean piping system. The cleaning media shall be as per testing media detailed on the line List.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: NATA Certified Pressure Test Report and Graph; 7: W
6.4.3 | 2014-09-22 | 2: Pressure Test Pipework 'Witness Test for any leaks'.; 3: S; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-005; 7: H
6.4.4 | 2014-09-22 | 2: Verification of cleanliness & dryness.; 3: I; 4: Hydrostatic Test Procedure, YSP-0000-M-001, 01707-PRO-PM-018; 5: AS 4041, YSP-0000-M-001; 6: 01707-ITR-ME-005; 7: W
7 |  | 2: SURFACE TREATMENT (TOUCH UPS)
7.1 | 2014-09-22 | 2: Protect surfaces not requiring treatment, e.g. Field welds. nameplates. machined surfaces.; 3: S; 4: SS-P120, Client Specifications; 5: SS-P120; 6: Visual Inspection; 7: SV
7.2 | 2014-09-22 | 2: Check the blast medium is to the specifications.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.3 | 2014-09-22 | 2: Check surface cleaning as per specification; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.4 | 2014-09-22 | 2: Monitor atmospheric conditions daily for Temperature (> 5 •c and <50 •c) and Humidity (>20% and <85%); 3: S; 5: SS-P120; 6: Visual Inspection or Bureau of Meteorology Data; 7: SV
7.5 | 2014-09-22 | 2: Check item to be painted (piping I steelwork etc.) for defects, damage. No welding flux, splatter, sharp edges etc. Confirm all inspections, NOT etc. on the item have been completed prior to painting.; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: H
7.6 | 2014-09-22 | 2: Ensure the items to be painted are adequately laid out and masked as needed; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.7 | 2014-09-22 | 2: Check correct paint is being used; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions, AFC drawings; 5: SS-P120; 6: Visual Inspection; 7: SV
7.8 | 2014-09-22 | 2: Ensure paints are mixed as per manufacturers recommendation; 3: S; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: Visual Inspection; 7: SV
7.9 | 2014-09-22 | 2: Check application is correct and is free of paint runs and other defects; 3: I; 4: SS-P120, Client Specifications, Manufacturers directions; 5: SS-P120; 6: DFT report; 7: SV
8 |  | 2: FINAL INSPECTION ON COMPLETION
8.1 | 2014-09-25 | 2: -Carry out final inspection -Generate punch list -Verification / clearance of punch list; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Field Inspection Checklist (FIC) 's Completions database; 7: H
9 |  | 2: FINALISE DOCUMENTATION
9.1 | 2014-09-25 | 2: Progressively check all test reports are correct.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: Reviewed and Approved ITR's; 7: H
9.2 | 2014-09-25 | 2: Sign off Inspection & Test Plan.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: ITP; 7: R
9.3 | 2014-09-25 | 2: MDR to be progressively compiled and submitted to client for final approval.; 3: I; 4: 01707-PLN-PM-002, Client Specifications, refer Note 1; 5: Client Specifications, refer Note 1; 6: MDR; 7: R
NOTES:
1 | CLIENT SPECIFICATIONS INCLUDING: YSP-0000-SPE-C-001, YSP-0000-SPE-C-002, YSP-0000-SPE-M-001, YSP-0000-SPE-S-002, YSP-0000-SPE-Y-001, YSP-0000-SPE-Y-003, YSP-2853-SPE-E-001, YSP-2880-SPE-J-001, YSP-2880-SPE-J-003, YSP-2880-SPE-J-005, YSP-2820-LST-P-004
2 | CLIENT SHALL BE GIVEN 24 HOURS NOTICE OF INSPECTION AND TEST ACTIVITY;