| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| ITP Ref / No.: |  |
| --- | --- |
| Location / Area / Lot |  |

| Item No | Description | Completed by |  | Accepted by |  | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| ITEMS TO BE CHECKED PRIOR TO APPROVAL |  | Initials | Date | Initials | Date |  |
|  | Define lots and set out works |  |  |  |  |  |
|  | Excavation permit approved and existing underground services/structures have been identified & marked on ground. |  |  |  |  |  |
|  | Expose any underground services/structures by hand /Vac Truck, if excavation permit specifies and not already completed by others. |  |  |  |  |  |
|  | Bedding and backfill material verified as compliant: - Sand in tranches for protection or bedding of Conduits shall comply with Table 7 of RVS-0000-SPE-Y-001 |  |  |  |  |  |
| Hold Point | Have items 1-4 been checked |  |  |  |  |  |
|  | Trench alignment pegged by surveyor has been boxed out (Survey Data Report) |  |  |  |  |  |
|  | Conduit trench is clear from rocks and debris, bedding material has been placed at a minimum of 100mm and is ready for conduit installation |  |  |  |  |  |
|  | Pit type and installation as per drawings |  |  |  |  |  |
|  | Galvanised steel sleeve placed for HME/LME road crossings, as per requirements |  |  |  |  |  |
|  | Conduit clean with 2no draw wires of suitable size for installation. Ends sealed as required. |  |  |  |  |  |
| Hold Point | Have items 5-9 been checked |  |  |  |  |  |
|  | Omni Ball markers placed every 30m and at changes of direction, cable slabs over conduit & buried services marker tape installed a minimum of 200mm above service. |  |  |  |  |  |
|  | Approve Backfill Sand: - Initial backfill material is Sand Fill shall be placed and compacted by hand and by means of hand tampers Initial backfill followed by lifts of general fill, compacted in 300mm layers, ref S1.003 |  |  |  |  |  |
|  | Cable route markers placed at 30m intervals and changes of direction. |  |  |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (NO PUNCHLIST ITEMS TO BE INCLUDED HERE) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |