| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| ACCOMODATION MODULE DISTRIBUTION BOARD |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item | Description |  |  | OK | N/A | Punch |
|  | Confirm mounting is firm, IP rating not compromised and not subject to vibration. |  |  |  |  |  |
|  | Confirm labelling is correct. |  |  |  |  |  |
|  | Confirm location and orientation is correct. |  |  |  |  |  |
|  | Confirm surface finish is undamaged (no paint chips). |  |  |  |  |  |
|  | Confirm door seal is secure and operation of latch and handle is unimpeded. |  |  |  |  |  |
|  | Confirm gland plate is earthed. |  |  |  |  |  |
|  | Confirm gland plate is secure and gasket in place. |  |  |  |  |  |
|  | Confirm glands are installed as per manufacturers recommendations and unused cable entries plugged. |  |  |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |  |  |
|  | Confirm ducting covers are fitted. |  |  |  |  |  |
|  | Confirm wiring is consistent with design drawings. |  |  |  |  |  |
|  | Confirm that the circuit schedule is correct, neat and located inside the DB with neutral numbers marked on circuits. |  |  |  |  |  |
|  | Confirm the SLD is present and circuits are identified correctly, legibly and indelibly. |  |  |  |  |  |
|  | Confirm terminal rails are secure and terminal numbering is in place and correct. |  |  |  |  |  |
|  | Confirm terminals are firmly tightened with one core per terminal. |  |  |  |  |  |
|  | Confirm rating, continuity and mechanical operation of the Main Isolator. |  |  |  |  |  |
|  | Confirm rating, continuity and mechanical operation of sub-circuit protective devices (CBs and RCDs). |  |  |  |  |  |
|  | Confirm Main Isolator, CBs and RCDs can be locked in the OFF position, oriented uniformly. |  |  |  |  |  |
|  | Confirm contactors and selector switches for correct installation, mechanical operation and damage. |  |  |  |  |  |
|  | Confirm that busbars are insulated and phase indication has been fitted where required. |  |  |  |  |  |
|  | Confirm any modifications correctly Red Lined and As Constructed drawings submitted. |  |  |  |  |  |
| ACCOMODATION MODULE DISTRIBUTION BOARD CONTINUITY, POLARITY/PHASING & EARTH / MEN N-E TEST |  |  |  |  |  |  |  |
| Test Equipment: |  | Serial No.: | Calibration Date: |  |  |  |  |
| Test Points |  | Resistance | Remarks |  |  |  |  |
| R-R |  | Ω |  |  |  |  |  |
| W-W |  | Ω |  |  |  |  |  |
| B-B |  | Ω |  |  |  |  |  |
| N-N |  | Ω |  |  |  |  |  |
| MEN-E |  | Ω |  |  |  |  |  |
| E-Gland Plate |  | Ω |  |  |  |  |  |
| E-Door |  | Ω |  |  |  |  |  |
| Main E-E |  | Ω |  |  |  |  |  |
| E-E Structural EP Bonding |  | Ω |  |  |  |  |  |
| Point to Point Confirmed Y N |  | Continuity Compliance Pass Fail | Isolator Operation Confirmed Y N |  |  |  |  |

| ACCOMODATION MODULE DISTRIBUTION BOARD INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  | Calibration Due Date: |  |  |
| Test Point | R to W | R to B | W to B | R to N | W to N | B to N | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| ACCOMODATION MODULE LIGHT AND SMALL POWER |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm equipment location is as per GA. |  |  |  |
|  | Confirm equipment earthing is of correct size, connected and tightened, all earthing arrangements are in place and labelled correctly as per applicable drawings. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm conduits, cable supporting structures and cable ties are installed as per specification. |  |  |  |
|  | Confirm luminaries, GPOs, switches and isolators are mounted correctly, structurally sound and sealed to prevent moisture ingress. |  |  |  |
|  | Confirm junction boxes are mounted correctly with all unused entries plugged and sealed to prevent moisture ingress. |  |  |  |
|  | Confirm junction boxes, GPOs, switches and isolators are all labelled in accordance with specification. |  |  |  |
|  | Confirm that lamps are correct type and wattage as per design. |  |  |  |
|  | Confirm that the polarity of luminaries and GPOs is correct. |  |  |  |
|  | Confirm all in-panel equipment including RCDs, CBs and earth leakage devices are rated and installed as per the design. |  |  |  |
|  | Confirm that DB circuit schedule is present in the distribution board and circuits are identified correctly, legibly. |  |  |  |
|  | Perform a point to point test and confirm continuity of phases and between main earth and all internal earthed equipment, devices, enclosure and other conductive parts. |  |  |  |
|  | Confirm applicable final sub-circuit neutral wires are correctly identified. |  |  |  |
|  | If applicable, confirm the MEN Link is clearly identified. |  |  |  |
|  | Confirm the Main Earth is clearly identified. |  |  |  |
|  | Confirm that control wiring has correct colour coding, sizing and is terminated correctly. |  |  |  |
|  | Perform and record all tests and checks as required in the Test Results table below. |  |  |  |

| Test Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Distribution Board |  |  |  |  |  |  |  | MEN Location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial Number: |  |  |  | Calibration Due Date: |  |  | Test Equipment: |  |  |  | Serial Number: |  |  |  |  | Calibration Due Date: |  |  |  |
| Circuit Description. | Circuit ID | CB/RCD/RCBO – Size/mA | Cable Type |  | Cable Size | Conduit / Cable Support Installed Correctly | Conduit and Junction Boxes Correctly Mounted & Sealed |  | Cable Terminations Correct and Confirmed for Tightness | Correct Circuit Cable Number(s)/ label/ Equip Tag Number |  | Confirm Equipment Type, Condition and Location Is Correct | No of Points per final sub-circuit | Polarity Correct |  | Insulation Resistance Result (MΩ) |  |  | Earth Continuity (Ω) |  | Drawings Red-lined As-Constructed & DB Circuit Schedule Reflects Installation | Circuit Left Safe Ready For Energisation |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Phase-E | Phase-N | N-E |  |  |  |  |
| Lighting | R1 | RCBO 10 A /30 mA | 2C+E |  | 1.5 mm2 | Yes | Yes |  | Yes | Yes |  | Yes | 10 | Yes |  | 500 MΩ | 500 MΩ | 500 MΩ | 0.3 Ω |  | Yes | Yes |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm enclosure surround and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |