| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset identification and physical asset label identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm commissioning energised stickers have been placed on equipment being energised. |  |  |  |
|  | Confirm that DB circuit schedule is present in the distribution board and circuits are identified correctly and legibly. |  |  |  |
|  | If applicable, confirm all downstream LV final sub-circuit or auxiliary circuits not part of this energisation are identified, under isolation, or disconnected and made safe. |  |  |  |
|  | Confirm all final sub-circuit Circuit Breaker(s)/ Isolator(s) are open prior to energisation. |  |  |  |
|  | If applicable, confirm all downstream LV final sub-circuit or auxiliary circuits not part of this energisation are identified, under isolation, or disconnected and made safe. |  |  |  |
|  | Confirm, if applicable, equipment arc flash rating has been identified and labelled. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and check of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all LV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | LV – as applicable, complete pre-energisation single phase 250 VDC insulation resistance tests(s), record the results in the tables provided. |  |  |  |
|  | Confirm Distribution Board isolator physically breaks circuit (all poles). |  |  |  |
|  | Confirm all internal IP2X covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm LV equipment has been left in the correct service position to support progressive energisation. |  |  |  |
|  | Confirm correct service locks are available and installed to support energisation. |  |  |  |

| 1ø PRE-ENERGISATION LV INSULATION RESISTANCE (IR) CHECK (250 VDC for 240 VAC) N/A |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. | Calibration Date: |  |  |
| Note: THIS IR confirmation check at operating voltage is intended to identify a change in IR state between the point in time that Construction Verification test was achieved and this final Pre-energisation check. Consideration must be given to the controlled battery limits of the check, inclusive of MEN connections, auxiliary supplies, equipment sensitivity, and any upstream and downstream induced voltage issues. IR tests may only be conducted using a suitable test voltage for which the circuit, equipment or device is capable of withstanding. |  |  |  |  |  |  |  |
| Test Point | A to E |  |  |  |  |  |  |
| Test Voltage | 250 VDC |  |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  |  |  |  |  |  |
| Insulation Resistance Compliance |  |  |  |  |  | Pass | Fail |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | If applicable, confirm the MEN Link is clearly identified and reinstated. |  |  |  |
|  | Re-confirm the distribution board isolator is in the correct position for switching. |  |  |  |
|  | Locally operate (Close) the distribution board feeder |  |  |  |
|  | Locally Close the Distribution Board MCB/Isolator. |  |  |  |
|  | Record voltage, polarity & phase rotation (Table) |  |  |  |
|  | Confirm mechanical circuit breaker position and indication elements are operating as per design. |  |  |  |
|  | Confirm outdoor lighting control is operating as per design (if applicable). |  |  |  |
|  | If applicable, once energised confirm the operation of the fire shut down relay. |  |  |  |
|  | For any final sub-circuits originating from the DB - Record RCD checks (Table). |  |  |  |
|  | For any final sub-circuits originating from the DB - Complete EFLI (Earth Fault Loop Impedance testing) if not satisfied by RCD check – complete table to measure Pass/Fail criteria (Table). |  |  |  |
|  | Record current draw – by embedded instrument indication or by physical test instrument measurement (Table). |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm equipment is left clean, free from debris and test tools. |  |  |  |
|  | Confirm correct access and control service locks are reinstated. |  |  |  |

| 1ø LOW VOLTAGE DISTRIBUTION BOARD POLARITY & VOLTAGE N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| LV Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: Line Side MCB/ISL |  | Load Side or Power Chassis |  |  |  |  |
| Test Points | Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 1ø A - N | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø A - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø Phase Supply Connection |  | Red Phase White Phase Blue Phase |  |  |  |  |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |  |

| POST-ENERGISATION RCD TEST N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. |  |  | Calibration Date: |  |  |
| Supply Voltage ________________ |  |  |  |  |  |  |  |  |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Input (mA) | Operating Time |  | Test Point |  | Voltage After Trip (All Poles) | Pass/Fail |
|  |  |  |  | 0o | 180o |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 - Breaker Trips in less than 0.4 Sec, Voltage is disconnected on all Poles. |  |  |  |  |  |  |  |  |  |

| POST-ENERGISATION EARTH FAULT LOOP IMPEDANCE (EFLI) TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Note: Not Required if a Positive RCD (Pass) Test has been Recorded. |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. | Calibration Date: |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Point |  | Measured/ Calculated Value | Pass/Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 – Measured value at the furthest point does not exceed maximum earth fault impedance Zs Ω for Circuit Breaker size. |  |  |  |  |  |  |

| LOW VOLTAGE SUPPLY – DISTRIBUTION BOARD STAGE 2 CURRENT DRAW |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  | Calibration Date: |
| Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: |  |  |  | Indicating Instrument: |  |  |
| Test Points | Applicable | Current Draw |  |  | Remarks |  |
| 1ø - A | N/A | Measured _______A Indicated _______A |  |  |  |  |
|  |  | Current draw within design or within name plate acceptable limits Y N |  |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | If applicable, confirm the MEN Link is clearly identified and reinstated. |  |  |  |
|  | Re-confirm the distribution board isolator is in the correct position for switching. |  |  |  |
|  | Locally operate (Close) the distribution board feeder |  |  |  |
|  | Locally Close the Distribution Board MCB/Isolator. |  |  |  |
|  | Record voltage, polarity & phase rotation (Table) |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm correct access and control service locks are reinstated. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |