| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |
| Manufacturer. | «ManufacturerName» |  |  |  | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |  |
| Drawing No. |  | «DocumentList» |  |  | Task No. |  | «TaskName» |
| Additional Information: |  | «Comments» |  |  |  |  |  |
| Air Cooled Split System Air Conditioner Manufacturers Data |  |  |  |  |  |  |  |
| Manufacturer |  |  |  |  |  |  |  |
| Outdoor Unit Model Number |  |  |  | Indoor Unit Model Number |  |  |  |
| Rated Capacity Cool (kW) |  |  |  | Rated Capacity Heat (kW) |  |  |  |
| Power Supply (1Ph/3Ph) |  |  |  |  |  |  |  |
| Power Input Cool (kW): |  |  |  | Power Input Heat (kW): |  |  |  |

| AIR COOLED SPLIT SYSTEM AIR CONDITIONER |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
| Note: This ITR is intended for Air-Cooled Split System Air-conditioners. For the purpose of this ITR, split system air-conditioners will be considered an Electrical Appliance for the purpose of installation and testing. The battery limits of the ITR Include the physical Installation of all hardware components, final sub-circuit protection, final sub-circuit power cabling, electrical Isolator, Indoor unit and outdoor unit interconnecting power & control cabling. It also includes interconnecting refrigerant pipes, pipe insulation, pipe supports and pressure testing and system evacuation. |  |  |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset identification and physical asset label identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm availability of Manufacturer’s Installation, Operation & Maintenance Manual. |  |  |  |
|  | If applicable, confirm availability of the Equipment Data Sheet (EDS). |  |  |  |
|  | Confirm Circuit Breaker(s)/ Isolator(s) are open prior to energisation. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and check of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all active terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Confirm supply voltage is in accordance with the electrical equipment name plate specification |  |  |  |
|  | Confirm Outdoor Unit isolator physically breaks circuit (all poles). |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Record voltage and polarity OUTDOOR UNIT (Table). |  |  |  |
|  | If applicable, Record voltage, polarity & phase rotation 3ø OUTDOOR UNIT (Table). |  |  |  |
|  | Record voltage and polarity INDOOR UNIT (Table). |  |  |  |
|  | If applicable for the equipment - record RCD checks (Table). |  |  |  |
|  | If applicable for the equipment - complete EFLI (Earth Fault Loop Impedance testing) if not satisfied by RCD check – complete table to measure Pass/Fail criteria (Table). |  |  |  |

| 1ø LOW VOLTAGE POLARITY & VOLTAGE (OUTDOOR UNIT) N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| LV Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |  |
| Test Points | Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 1ø A - N | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø A - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø Phase Supply Connection |  | Red Phase White Phase Blue Phase |  |  |  |  |
| Phase Indication |  | Phase Indication Installed |  |  | Phase Indication Functioning |  |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |  |

| 3ø LOW VOLTAGE POLARITY, VOLTAGE & PHASE ROTATION (OUTDOOR UNIT) N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| LV Supply Voltage: 415 VAC Other ______________ |  |  |  |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 3ø R - R | N/A Phasing OK |  |  |  |  | Pass Fail |
| 3ø W - W | N/A Phasing OK |  |  |  |  | Pass Fail |
| 3ø B - B | N/A Phasing OK |  |  |  |  | Pass Fail |
| 3ø R - W |  | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - B |  | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø W - B |  | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø W - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø B - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø W - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø B - E | Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø (RWB) Phase Rotation |  | RWB Clockwise |  |  | RWB Anti-Clockwise |  |
| Phase Indication |  | Phase Indication Installed |  |  | Phase Indication Functioning |  |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |  |

| 1ø LOW VOLTAGE POLARITY & VOLTAGE (INDOOR UNIT) N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| LV Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |
| Test Points | Polarity OK | Voltage Result |  |  | Pass/Fail |
| 1ø A - N | Polarity OK | Measured _______ |  |  | Pass Fail |
| 1ø A - E | Polarity OK | Measured _______ |  |  | Pass Fail |
| 1ø CTL1 - N | Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | Polarity OK | Measured _______ |  |  | Pass Fail |
| 1ø Phase Supply Connection |  | Red Phase White Phase Blue Phase |  |  |  |
|  |  | Polarity & Voltage Acceptable Y N |  |  |  |

| POST-ENERGISATION RCD TEST N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. |  |  | Calibration Date: |  |  |
| Supply Voltage ________________ |  |  |  |  |  |  |  |  |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Input (mA) | Operating Time |  | Test Point |  | Voltage After Trip (All Poles) | Pass/Fail |
|  |  |  |  | 0o | 180o |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 - Breaker Trips in less than 0.4 Sec, Voltage is disconnected on all Poles. |  |  |  |  |  |  |  |  |  |

| POST-ENERGISATION EARTH FAULT LOOP IMPEDANCE (EFLI) TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Note: Not Required if a Positive RCD (Pass) Test has been Recorded. |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. | Calibration Date: |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Point |  | Measured/ Calculated Value | Pass/Fail |
|  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 – Measured value at the furthest point does not exceed maximum earth fault impedance Zs Ω for Circuit Breaker size. |  |  |  |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm AC Controller works in all modes and selections. |  |  |  |
|  | Confirm Indoor unit filters are clean. |  |  |  |
|  | Check indoor unit for excessive vibration. |  |  |  |
|  | Confirm Cooling cycle operates. |  |  |  |
|  | Confirm Heating cycle operates. |  |  |  |
|  | Confirm outdoor unit for excessive vibration and or noise. |  |  |  |
|  | Complete Pressure Check and Temperature Table. |  |  |  |
|  | Check condensate drain discharges via gravity and P-Trap, if installed, operates |  |  |  |
|  | Confirm low volt shut down permissives are operating as per design (if applicable). |  |  |  |
|  | Confirm fire shut down permissives are operating as per design (if applicable). |  |  |  |
|  | Record current draw (Table). |  |  |  |

| REFRIGERANT PRESSURE & TEMPERATURE |  |  |
| --- | --- | --- |
| Note: Operating test to be carried out in either heating or cooling cycles under the highest load possible under the prevailing environmental conditions. Pressure results must have stabilised and be within the manufacturers specifications. |  |  |
| Refrigerant Charge | R410A R30 Other __________ |  |
| Liquid Line | _________kPA | Pass Fail |
| Gas Line | _________kPa | Pass Fail |
| Ambient Temperature | Indoor_________ CO | Outdoor_________ CO |
| AC Temperature | Indoor Unit Evaporator Coil | Outdoor Unit Condenser Coil |
|  | Air On _____ CO | Air On _____ CO |
|  | Air Off _____ CO | Air Off _____ CO |
| Condensate Drain Test | Pass Fail |  |
| AC Operational Tests Confirmed |  | Y N |

| LOW VOLTAGE SUPPLY – STAGE 2 CURRENT DRAW |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  | Calibration Date: |
| Supply Voltage: 240 VAC 415 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: |  |  |  | Indicating Instrument: |  |  |
| Test Points | Applicable | Current Draw |  |  | Remarks |  |
| 1ø - A | N/A | Measured _______A |  |  |  |  |
| 3ø - R | N/A | Measured _______A |  |  |  |  |
| 3ø - W | N/A | Measured _______A |  |  |  |  |
| 3ø - B | N/A | Measured _______A |  |  |  |  |
|  |  | Current draw within design or within name plate acceptable limits Y N |  |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |
|  | This form must be completed by a qualified and endorsed ARC Refrigerant Handling Licenced Installer. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Signature: |  | Date: |  | Date: |  |
| Name: |  |  |  |  |  |
| RHL No.: |  |  |  |  |  |
| Date: |  |  |  |  |  |