| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset identification and physical asset label identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm availability of Manufacturer’s Installation, Operation & Maintenance Manual. |  |  |  |
|  | Confirm availability of the Equipment Data Sheet (EDS). |  |  |  |
|  | Confirm availability of Battery Cell Safety Data Sheet and appropriate PPE is identified and available. |  |  |  |
|  | Confirm commissioning energised stickers have been placed on equipment being energised. |  |  |  |
|  | Confirm Circuit Breaker(s)/ Isolator(s) are open prior to energisation. |  |  |  |
|  | If applicable, confirm all downstream ELV & LV final sub-circuit or auxiliary circuits not part of this energisation are identified, under isolation, or disconnected and made safe. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and confirm of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all ELV & LV Battery Charger terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all ELV Battery terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Confirm, if applicable, all Battery cells have the correct Electrolyte Level |  |  |  |
|  | Confirm Battery cabinet air extraction systems or cross flow ventilation systems are operational prior to battery charging. |  |  |  |
|  | Confirm Battery Strings are physically disconnected / Isolated. |  |  |  |
|  | Confirm battery isolator(s) physically breaks circuit (all poles). |  |  |  |
|  | Confirm all post energisation physical test and verification points have been identified and applicable Arc Flash category PPE identified and available. |  |  |  |
|  | Confirm LV Battery equipment has been left in the correct service position to support progressive energisation. |  |  |  |

| STAGE 2 BATTERY STRING ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | For each battery string confirm the battery cell quantity, types and connections are as per design and record voltage and polarity for each connected string (Table). |  |  |  |

| BATTERY STRING EXTRA LOW VOLTAGE BATTERY SUPPLY – POLARITY & VOLTAGE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  |  | Serial No.: |  |  | Calibration Date: |  |  |
| Battery System Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |  |  |  |  |  |
| BATTERY STRING 1 |  |  |  |  |  |  |  |  |  |  |
| Battery String Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |  |  |  |  |  |
| Cell Voltage: |  |  | Cell Rating AH: |  |  |  | Number of Cells in String: |  |  |  |
| Test Points | Applicable / Polarity OK |  |  | Voltage Result |  |  |  |  | Pass/Fail |  |
| A - N | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| A - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| N - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| BATTERY STRING 2 N/A |  |  |  |  |  |  |  |  |  |  |
| Battery String Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |  |  |  |  |  |
| Cell Voltage: |  |  | Cell Rating AH: |  |  |  | Number of Cells in String: |  |  |  |
| Test Points | Applicable / Polarity OK |  |  | Voltage Result |  |  |  |  | Pass/Fail |  |
| A - N | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| A - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| N - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| BATTERY STRING 3 N/A |  |  |  |  |  |  |  |  |  |  |
| Battery String Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |  |  |  |  |  |
| Cell Voltage: |  |  | Cell Rating AH: |  |  |  | Number of Cells in String: |  |  |  |
| Test Points | Applicable / Polarity OK |  |  | Voltage Result |  |  |  |  | Pass/Fail |  |
| A - N | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| A - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| N - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| BATTERY STRING 4 N/A |  |  |  |  |  |  |  |  |  |  |
| Battery String Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |  |  |  |  |  |
| Cell Voltage: |  |  | Cell Rating AH: |  |  |  | Number of Cells in String: |  |  |  |
| Test Points | Applicable / Polarity OK |  |  | Voltage Result |  |  |  |  | Pass/Fail |  |
| A - N | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| A - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| N - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |

| STAGE 2 BATTERY STRING ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Connect Battery strings in Series or Parallel as per design. |  |  |  |
|  | For the overall Battery System record voltage and polarity for the total system (Table). |  |  |  |
|  | Re-confirm the battery Charger Battery system Isolators are OPEN. |  |  |  |

| BATTERY SYSTEM OVERALL EXTRA LOW VOLTAGE BATTERY SUPPLY – POLARITY & VOLTAGE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  |  | Serial No.: |  |  | Calibration Date: |  |  |
| Battery System Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |  |  |  |  |  |
| System Voltage: |  |  | Overall Rating AH: |  |  |  | Total Number of Cells in System: |  |  |  |
| Test Points | Applicable / Polarity OK |  |  | Voltage Result |  |  |  |  | Pass/Fail |  |
| A - N | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| A - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
| N - E | Polarity OK |  |  | Measured _______ |  |  |  |  | Pass Fail |  |
|  |  |  |  | Overall Polarity & Voltage, Acceptable Y N |  |  |  |  |  |  |

| STAGE 2 BATTERY CHARGER ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Energise the battery charger supply circuit. |  |  |  |
|  | Record charger supply voltage, polarity (Table). |  |  |  |
|  | Confirm charger control panel communication - status and indication. |  |  |  |
|  | Confirm PLC I/O - status, indication and values. |  |  |  |
|  | Confirm charger control panel selector switches operate as per design. |  |  |  |
|  | Confirm charger control panel push buttons operate as per design. |  |  |  |
|  | Confirm charger control panel indicators, indicate and operate as per design. |  |  |  |
|  | Confirm, if applicable, charger control panel mechanical and electrical changeover interlocks operate as per design. |  |  |  |
|  | Confirm SCADA - status, indication and values. |  |  |  |
|  | Confirm low volt shut down permissives are operating as per design (if applicable). |  |  |  |
|  | Confirm fire shut down permissives are operating as per design (if applicable). |  |  |  |

| BATTERY CHARGER SUPPLY - POLARITY, VOLTAGE & PHASE ROTATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| Supply Voltage: 240 VAC 415 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: Line Side MCB/ISL |  | Load Side or Power Chassis |  |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 1ø A - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 1ø A - E | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - W | N/A | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - B | N/A | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø W - B | N/A | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø W - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø B - N | N/A Polarity OK | Measured _______ Indicated _______ |  |  |  | Pass Fail |
| 3ø R - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø W - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø B - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø (RWB) Phase Rotation N/A |  | RWB Clockwise |  |  | RWB Anti-Clockwise |  |
| Phase Indication |  | Phase Indication Installed |  |  | Phase Indication Functioning |  |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |  |

| STAGE 2 BATTERY SYSTEM ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |  |
|  | Confirm Battery Isolator(s) are closed. |  |  |  |  |
|  | Confirm Battery Charger ELV Output Polarity and Voltage. |  |  |  |  |
|  | Confirm Battery Charger healthy In-service status, Alarms, trips and Charge monitoring. |  |  |  |  |
|  | Confirm battery charger operates as per design observing charging and maintenance cycles. |  |  |  |  |
|  | Record Battery Charger Input Load current draw. |  |  |  |  |
|  | Record Battery Charger ELV Output current load. |  |  |  |  |
|  | Confirm by Infrared imaging that all ELV battery, Links, Terminals and battery cable connections are not experiencing any increase (outlier) in temperature reflecting a poor termination. |  |  |  |  |
|  | Confirm by Infrared imaging that all ELV battery cells are not experiencing any increase (outlier) in temperature reflecting a poor cell health. |  |  |  |  |

| BATTERY CHARGER OUTPUT EXTRA LOW VOLTAGE BATTERY SUPPLY – POLARITY & VOLTAGE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| Battery Charger System Voltage: 12 VDC 24 VDC 48 VDC 110 VDC Other ______________ |  |  |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  | Pass/Fail |
| A - N | Polarity OK | Measured _______ |  |  | Pass Fail |
| A - E | Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | Polarity OK | Measured _______ |  |  | Pass Fail |
|  |  | Overall Polarity & Voltage, Acceptable Y N |  |  |  |

| BATTERY CHARGER LOW VOLTAGE SUPPLY – STAGE 2 CURRENT DRAW |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  | Calibration Date: |
| Supply Voltage: 240 VAC 415 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: |  |  |  | Indicating Instrument: |  |  |
| Test Points | Applicable | Current Draw |  |  | Remarks |  |
| 1ø - A | N/A | Measured _______A Indicated _______A |  |  |  |  |
| 3ø - R | N/A | Measured _______A Indicated _______A |  |  |  |  |
| 3ø - W | N/A | Measured _______A Indicated _______A |  |  |  |  |
| 3ø - B | N/A | Measured _______A Indicated _______A |  |  |  |  |
|  |  | Current draw within design or within name plate acceptable limits Y N |  |  |  |  |

| BATTERY ELV SYSTEM CHARGING – STAGE 2 CURRENT DRAW |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 240 VAC 415 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: |  |  |  | Indicating Instrument: |  |  |
| Test Points | Applicable | Current Draw |  |  |  | Remarks |
| A |  | Measured _______A Indicated _______A |  |  |  |  |
|  |  | Current output within design or within name plate acceptable limits Y N |  |  |  |  |

| STAGE 2 BATTERY SYSTEM ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Remove battery charger supply and observe battery charger management system, system current, system voltage and indicators operate as per design. Load and discharge testing to be completed in Stage 3. |  |  |  |
|  | Confirm system stability and regularly observe the charging cycle through bulk or constant charge modes until battery system approaches full charge and the charging system switches to float or equalisation mode. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm correct access and control service locks are installed. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |