| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Manufacturer. | «ManufacturerName» |  |  | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |  |
| Drawing No. | «DocumentList» |  |  | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |  |  |
| BATTERY CHARGER AND BATTERY DATA |  |  |  |  |  |
| Manufacturer: |  |  | Charger Rating: |  |  |
| Serial No.: |  |  | Battery Rating (Ah): |  |  |
| Model No.: |  |  | Battery Voltage: |  |  |
| Charger Input Supply Voltage: |  |  | Type of Cells: |  |  |
| Charger Output Voltage: |  |  | Number of Cells: |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm equipment is safely isolated and battery strings are disconnected. |  |  |  |
|  | Confirm Nameplate Details are as per Datasheet and Equipment Labelling is as per GA and Schematic. |  |  |  |
|  | Confirm Layout, location and orientation is correct against design drawings. |  |  |  |
|  | Confirm equipment is level, Battery Cells are contained and supported with clearance and ventilation distances as per design. |  |  |  |
|  | Confirm thermal and cross flow ventilation is not physically impeded and is unobstructed beyond the design requirements. |  |  |  |
|  | Confirm installation is not blocking access for equipment removal and is not a hazard to personnel. |  |  |  |
|  | Confirm the quantity of Cells and Cell size and type is as per design. |  |  |  |
|  | Confirm that the cells have been wired correctly and polarity is in accordance with the design. |  |  |  |
|  | Confirm that all connections are tight, and all linkage bars are secure shrouded and protected. |  |  |  |
|  | If applicable, confirm that electrolyte level is correct. |  |  |  |
|  | Confirm that a layer of approved grease has been applied to the ELV battery terminations. |  |  |  |
|  | Confirm that cables are numbered and colour coded correctly at both ends as per the cable schedule. |  |  |  |
|  | Confirm equipment is free from damage and debris internally and externally. |  |  |  |
|  | Confirm cable glands are correct size/type and installed correctly installed. |  |  |  |
|  | Confirm earthing of equipment is correct as per design drawings. |  |  |  |
|  | If applicable, operate door and confirm that handle and locking mechanism move freely. |  |  |  |
|  | If applicable, confirm that the integrity of door seals or gasket are intact. |  |  |  |
|  | If applicable, confirm that all earthing is as per design complete on doors, internal components and gland plates. |  |  |  |
|  | Confirm that internal wiring is consistent with design drawings and mark-up as necessary. |  |  |  |
|  | Confirm cable ducting is secure and complete with covers and not distorted. |  |  |  |
|  | Confirm Wiring looms are neat and straight where no ducting exists. |  |  |  |
|  | Confirm that ferrule numbers are correct as per design drawings. |  |  |  |
|  | Confirm cable terminations to confirm all lugs/pins are crimped correctly and terminals are clean and dust free. |  |  |  |
|  | Confirm terminal rails are secure, terminals installed correctly, and terminal numbering is correct and in place. |  |  |  |
|  | Confirm separation and segregation of ELV and LV voltages and suitable IP2X shrouding is installed. |  |  |  |
|  | - Confirm rating and continuity of fuses, and confirm mechanical operation of MCBs. |  |  |  |
|  | - Confirm the installation of control relays and labelling. |  |  |  |
|  | - Confirm that contactors and selector switches are undamaged and installed correctly. |  |  |  |

| COMPLETION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | - Confirm all cables are reconnected, correctly tensioned and all covers are replaced. |  |  |  |
|  | - Confirm final cell connections are left isolated/disconnected in preparation for stage 2 energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |