| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cable Type: | «CableType» |  | Cable Rating: | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Physical Checks | (Pre-Inspection Comment) |
| --- | --- |
| Drum Number |  |
| Drum Condition |  |
| Cable Condition |  |

| LOW VOLTAGE CABLE N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CONTINUITY TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  |  | Serial No.: |  |  |  |  | Calibration Date: |  |  |
| Test Points |  |  | Point to Point Check (Initial Pass/Fail) |  |  |  |  | Continuity Check – Result Ω |  |  |  |  |
| R |  |  | R-R |  |  |  |  | Ω |  |  |  |  |
| W |  |  | W-W |  |  |  |  | Ω |  |  |  |  |
| B |  |  | B-B |  |  |  |  | Ω |  |  |  |  |
| N |  |  | N-N |  |  |  |  | Ω |  |  |  |  |
| E |  |  | E-E |  |  |  |  | Ω |  |  |  |  |
|  |  |  | Point to Point Confirmed Y N |  |  |  |  | Continuity Compliance Pass Fail |  |  |  |  |
| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment |  |  |  | Serial No. |  |  |  |  | Calibration Date: |  |  |  |
| Test Point | R to W | R to B |  | W to B |  | R to N | W to N |  | B to N |  | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500kVDC |  | 500 VDC |  | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  |  |  | Pass | Fail |

| HIGH VOLTAGE CABLE N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CONTINUITY TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No.: |  |  |  | Calibration Date: |  |  |  |  |  |
| Test Connections |  |  | Point to Point Check (Initial Pass/Fail) |  |  |  | Continuity Check – Result Ω |  |  |  |  |  |
| R-R:Scn |  |  | R-R |  |  |  | Ω |  |  |  |  |  |
| W-W:Scn |  |  | W-W |  |  |  | Ω |  |  |  |  |  |
| B-B:Scn |  |  | B-B |  |  |  | Ω |  |  |  |  |  |
|  |  |  | Point to Point Confirmed Y N |  |  |  | Continuity Compliance Pass Fail |  |  |  |  |  |
| CONDUCTOR INSULATION RESISTANCE TEST N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment |  |  |  | Serial No. |  |  |  | Calibration Date: |  |  |  |  |
| Test Point | R to R:Screen | B to B:Screen |  | W to W:Screen | R to W | W to B |  |  | B to R |  | RWB to E |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC | 5 kVDC | 5 kVDC |  |  | 5 kVDC |  | 5 kVDC |  |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ | MΩ | MΩ |  |  | MΩ |  | MΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  |  | Pass |  | Fail |

| FIBRE OPTIC CABLE TESTING N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Fibre optic cable meets all the requirements specifications SS-T011 and SS-T024. Any deviations must be approved in writing by the Engineer. |  |  |  |
|  | Fibre optic cable and drum are free from damage. |  |  |  |
|  | Confirm that the fibre sheath is free from mechanical damage. |  |  |  |
|  | Confirm manufacturer’s cable drum tests supplied and/or cable vendor certification received. If suitable they can be approved by the Engineer prior to installation of cable. (Attach to ITR) |  |  |  |
|  | If manufacturer’s cable drum tests have not been supplied and/or cable vendor certification is not in evidence then the following On-Drum tests are required prior to installation. |  |  |  |
|  | Pre-installation drum OTDR tests completed on at least one core per tube with a minimum of 10% of all fibre cores tested on the cable. Native digital and PDF trace test results supplied. |  |  |  |
|  | SMOF - Bi-directional OTDR testing completed at 1310nm, 1550nm and 1625nm for all SMOF cores. Native digital OTDR trace files, viewing software and PDF trace files to be submitted to the Engineer for review. All cores pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |
|  | MMOF - Bi-directional insertion loss tests completed at 850nm & 1300nm for all MMOF cores. Results populated in test result form attached and submitted to the Engineer for review. All cores pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |

| COMPLETION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch | Comment |
|  | Confirm cables are fully discharged from testing. |  |  |  |  |
|  | Confirm Cable Drums are suitably numbered and identified to support traceability. |  |  |  |  |
|  | Confirm all cable ends are suitably capped and protected from moisture ingress. |  |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on drawings and model as per project procedures. |  |  |  |
|  | As applicable this form must be completed by an Authorised Electrical Worker or a AMCA Registered Cabler. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Registration No.: |  | Date: |  | Date: |  |
| Date: |  |  |  |  |  |