| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Drawing No. | «DocumentList» |  | Task No. | «TaskName» |
| Additional Information: |  | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm that installation is in accordance with structural layout drawing. |  |  |  |
|  | Confirm that support brackets and fixings are structurally sound and not subject to vibration. |  |  |  |
|  | Confirm that support brackets and fixings are installed at correct intervals for type of cable support, in accordance with manufacturer’s specification. |  |  |  |
|  | Confirm that paint work integrity has been maintained where supports are attached and any damage to the support galvanizing is reinstated to original state. |  |  |  |
|  | Confirm that cable ladder, tray or duct alignment is maintained and mounted squarely. |  |  |  |
|  | Confirm that all sharp edges and burrs have been removed from the cable ladder, tray, duct or conduit. Confirm all open ended conduits are fitted with Polymer bushings. |  |  |  |
|  | Confirm that where steel (or metal) structures, ladders, trays or conduits are used, that appropriate precautions have been made to protect these structures, and the structures onto which they are installed, from corrosion resulting from contact between dissimilar metals |  |  |  |
|  | Confirm the construction of manufactured sets and bends meets the requirements for structural integrity and uniformity, in accordance with manufacturer’s specification. |  |  |  |
|  | Confirm cable ladder EP Bonding is installed in the correct locations and that bonding is of the correct size and lugs are crimped correctly. |  |  |  |
|  | Confirm for all non-metallic cable supports that they have been supplied, stored and installed as per the manufacturers recommendations and suitable UV protection has been achieved as per these recommendations. |  |  |  |
|  | Confirm horizontal and vertical segregation of cable trays and cables is maintained, where required (HV, LV, communications and ELV cables). |  |  |  |
|  | Confirm that barrier strip is installed in as per design. |  |  |  |
|  | Confirm that expansion joints have been installed in ladder runs greater than 50 m. |  |  |  |
|  | Confirm that conduits are fastened to structures at no more than 1500 mm intervals. |  |  |  |
|  | Confirm all penetrations and fire barriers are sealed with the appropriately rated fire sealant. |  |  |  |
|  | Confirm that sun cover anchoring arrangement is installed correctly. |  |  |  |
|  | Confirm any applicable modifications are red lined on the applicable schematic and As Constructed drawings submitted. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |