| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Drawing No. | «DocumentList» |  | Task No. | «TaskName» |
| Additional Information: |  | «Comments» |  |  |

| TEST EQUIPMENT |  |  |
| --- | --- | --- |
| Test Equipment | Serial No. | Calibration Due Date |

| TEST POSITIONS CARRIED OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Note: Provide description below and attach layout drawing/ Sketch to indicate test point locations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item | Description |  |  |  |  |  |  |  |  |  | PASS |  | FAIL |  | Punch |  |
| 1 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |  |  |
| TEST RESULTS: (all results in micro Ohms) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TEST POSITION |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 10 |  | 11 |  | 12 |
| RED PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| WHITE PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BLUE PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NEUTRAL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EARTH |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Practical methods for Contact Resistance test and acceptance criteria: - In all cases a four wire contact resistance tester shall be used. - Where multiple readings of similar sorts of connections are taken, then these should produce similar results. Where results deviate on the higher resistance side from the average or where a result is a clear outlier, then the joint should be classified as suspect and a decision to re-terminate is in order. - The resistance of the joint must be no worse than the conductor resistance located at either side of the termination. - As a rule of thumb, the test current should not exceed the rated current of the equipment under test. The test current should typically be at 10% of the rated current. The test current should not exceed the manufacturer’s specification. Main Earth connections should be tested at 100 A, and not exceed 0.5 Ω. - Typically, contact resistance testers come in 10 A, 50 A and 100 A DC versions. Selecting a test current will need to accommodate the standard range of test currents. In practical applications, test currents above 100 A will not be required. Any contact resistance testing beyond 100 A will be at the request of the engineer and will be supported by the specialised equipment required. - In-field testing, not undertaken in controlled environments, will need to consider environmental conditions when evaluating and approving test results. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |