| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |

| STAGE 2 PRE-ENERGISATION HOLD POINTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset identification and physical asset label identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm availability of Manufacturer’s Installation, Operation & Maintenance Manual. |  |  |  |
|  | If applicable, confirm availability of the Equipment Data Sheet (EDS). |  |  |  |
|  | Confirm commissioning energised stickers have been placed on equipment being energised. |  |  |  |
|  | Confirm Circuit Breaker(s)/ Isolator(s) are open prior to energisation. |  |  |  |
|  | If applicable, confirm all downstream LV final sub-circuit or auxiliary circuits not part of this energisation are identified, under isolation, or disconnected and made safe. |  |  |  |
|  | If applicable, confirm all downstream ELV auxiliary circuits not part of this energisation are identified, disconnected and made safe. |  |  |  |
|  | Confirm, if applicable, equipment arc flash rating has been identified and labelled. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and confirm of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all LV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | As applicable, complete pre-energisation single phase 250 VDC or three phase 500 VDC insulation resistance tests(s), record the results in the tables provided. |  |  |  |
|  | Confirm panel isolator physically breaks circuit (all poles). |  |  |  |

| 1ø PRE-ENERGISATION LV INSULATION RESISTANCE (IR) CHECK (250 VDC for 240 VAC) N/A |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. | Calibration Date: |  |  |
| Note: THIS IR confirmation check at operating voltage is intended to identify a change in IR state between the point in time that Construction Verification test was achieved and this final Pre-energisation check. Consideration must be given to the controlled battery limits of the check, inclusive of MEN connections, auxiliary supplies, equipment sensitivity, and any upstream and downstream induced voltage issues. IR tests may only be conducted using a suitable test voltage for which the circuit, equipment or device is capable of withstanding. |  |  |  |  |  |  |  |
| Test Point | A to E |  |  |  |  |  |  |
| Test Voltage | 250 VDC |  |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  |  |  |  |  |  |
| Insulation Resistance Compliance |  |  |  |  |  | Pass | Fail |

| 3ø PRE-ENERGISATION LV INSULATION RESISTANCE (IR) CHECK (500 VDC for 415 VAC) N/A |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. |  |  | Calibration Date: |  |  |  |  |
| Note: This IR confirmation check at operating voltage is intended to identify a change in IR state between the point in time that Construction Verification test was achieved and this final Pre-energisation check. Consideration must be given to the controlled battery limits of the check, inclusive of MEN connections, VTs and protection elements, auxiliary supplies, equipment sensitivity, and any upstream and downstream induced voltage issues. IR tests may only be conducted using a suitable test voltage for which the switchgear, circuit, equipment or device is capable of withstanding. |  |  |  |  |  |  |  |  |  |  |  |
| Test Point | R to W | R to B | W to B |  |  |  |  |  |  | RWB to E |  |
| Test Voltage | 500 VDC | 500 VDC | 500 VDC |  |  |  |  |  |  | 500 VDC |  |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ |  |  |  |  |  |  | MΩ |  |
| Insulation Resistance Compliance |  |  |  |  |  |  |  |  | Pass |  | Fail |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all internal IP2X covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm LV equipment has been left in the correct service position to support progressive energisation. |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | De-isolate and confirm, if applicable, live line (Phase Indicators) work as per design. |  |  |  |
|  | If applicable, confirm panel local E-Stop operates as per design. |  |  |  |
|  | Record voltage, polarity & phase rotation (Table) – desired RWB Clockwise. |  |  |  |
|  | Record auxiliary voltages (Table). |  |  |  |
|  | If applicable for any final sub-circuits originating from the Control Panel - record RCD checks (Table). |  |  |  |
|  | If applicable for any final sub-circuits originating from the Control Panel - complete EFLI (Earth Fault Loop Impedance testing) if not satisfied by RCD check – complete table to measure Pass/Fail criteria (Table). |  |  |  |

| 1ø LOW VOLTAGE POLARITY & VOLTAGE N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| LV Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: Line Side MCB/ISL |  | Load Side or Power Chassis |  |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 1ø A - N | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø A - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø Phase Supply Connection |  | Red Phase White Phase Blue Phase |  |  |  |  |
| Phase Indication |  | Phase Indication Installed |  |  | Phase Indication Functioning |  |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |  |

| 3ø LOW VOLTAGE POLARITY, VOLTAGE & PHASE ROTATION N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| LV Supply Voltage: 415 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: Line Side MCB/ISL |  | Load Side or Power Chassis |  |  | Lighting Chassis |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 3ø R - R | N/A Phasing OK |  |  |  |  | Pass Fail |
| 3ø W - W | N/A Phasing OK |  |  |  |  | Pass Fail |
| 3ø B - B | N/A Phasing OK |  |  |  |  | Pass Fail |
| 3ø R - W | N/A | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - B | N/A | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø W - B | N/A | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø W - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø B - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  |  | Pass Fail |
| 3ø R - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø W - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø B - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 3ø (RWB) Phase Rotation |  | RWB Clockwise |  |  | RWB Anti-Clockwise |  |
| Phase Indication |  | Phase Indication Installed |  |  | Phase Indication Functioning |  |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |  |

| EXTRA LOW & LOW VOLTAGE AUXILIARY SUPPLY - POLARITY, VOLTAGE & PHASE ROTATION N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 240 VAC 415 VAC Other ______________ |  |  |  |  |  |
| Test Location: Line Side MCB/ISL |  | Load Side or Power Chassis |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  | Pass/Fail |
| 1ø A - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  | Pass Fail |
| 1ø A - E | N/A Polarity OK | Measured _______ Indicated ________ |  |  | Pass Fail |
| 3ø R - W | N/A | Measured _______ Indicated ________ |  |  | Pass Fail |
| 3ø R - B | N/A | Measured _______ Indicated ________ |  |  | Pass Fail |
| 3ø W - B | N/A | Measured _______ Indicated ________ |  |  | Pass Fail |
| 3ø R - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  | Pass Fail |
| 3ø W - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  | Pass Fail |
| 3ø B - N | N/A Polarity OK | Measured _______ Indicated _______ |  |  | Pass Fail |
| 3ø R - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| 3ø W - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| 3ø B - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |  |  |

| POST-ENERGISATION RCD TEST N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. |  |  | Calibration Date: |  |  |
| Supply Voltage ________________ |  |  |  |  |  |  |  |  |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Input (mA) | Operating Time |  | Test Point |  | Voltage After Trip (All Poles) | Pass/Fail |
|  |  |  |  | 0o | 180o |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 - Breaker Trips in less than 0.4 Sec, Voltage is disconnected on all Poles. |  |  |  |  |  |  |  |  |  |

| POST-ENERGISATION EARTH FAULT LOOP IMPEDANCE (EFLI) TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Note: Not Required if a Positive RCD (Pass) Test has been Recorded. |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. | Calibration Date: |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Point |  | Measured/ Calculated Value | Pass/Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 – Measured value at the furthest point does not exceed maximum earth fault impedance Zs Ω for Circuit Breaker size. |  |  |  |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm communication - status and indication. |  |  |  |
|  | Confirm Safety Related Control Function (SRCF) PLC I/O - Status, Indication and Values. |  |  |  |
|  | Confirm Protective Related Control Function (PRCF) PLC I/O - Status, Indication and Values. |  |  |  |
|  | Confirm panel selector switches operate as per design. |  |  |  |
|  | Confirm panel push buttons operate as per design. |  |  |  |
|  | Confirm panel indicators, indicate and operate as per design. |  |  |  |
|  | Confirm panel status, semaphores and position indicators are operating as per design. |  |  |  |
|  | Confirm panel mechanical and electrical interlocks operate as per design. |  |  |  |
|  | Confirm panel SCADA - status, indication and values. |  |  |  |
|  | Confirm low volt shut down permissives are operating as per design (if applicable). |  |  |  |
|  | Confirm fire shut down permissives are operating as per design (if applicable). |  |  |  |
|  | Record current draw – by embedded instrument indication or physical test instrument measurement (Table). |  |  |  |

| LOW VOLTAGE SUPPLY – STAGE 2 CURRENT DRAW |  |  |  |
| --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: | Calibration Date: |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 240 VAC 415 VAC Other ______________ |  |  |  |
| Test Location: |  | Indicating Instrument: |  |
| Test Points | Applicable | Current Draw | Remarks |
| 1ø - A | N/A | Measured _______A Indicated _______A |  |
| 3ø - R | N/A | Measured _______A Indicated _______A |  |
| 3ø - W | N/A | Measured _______A Indicated _______A |  |
| 3ø - B | N/A | Measured _______A Indicated _______A |  |
|  |  | Current draw within design or within name plate acceptable limits Y N |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm correct access and control service locks are installed. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |