| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| STAGE 4 LOAD TEST PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm availability of Manufacturer’s Installation, Operation & Maintenance Manual (IOM/TMAN). |  |  |  |
|  | Record indicated or measured Load voltage & current (Table) |  |  |  |
|  | Record auxiliary Load voltages & current (Table). |  |  |  |
|  | Confirm panel indicators, indicate and operate as per design. |  |  |  |
|  | Confirm SCADA - status, indication and values. |  |  |  |
|  | Confirm that the equipment is functioning as per design and all results, indicated or measured are within manufacturer’s specifications. |  |  |  |
|  | Confirm that the equipment is functioning within the design operating / protection parameters. |  |  |  |
|  | Confirm equipment / system stability and reliability under load |  |  |  |
|  | Where practical undertake an Infra-Red temperature survey, record and attach images in the supporting documentation table. |  |  |  |
|  | Identify and attach in the table below any relevant supporting documentation |  |  |  |
|  | Identify and attach in the table below any Vendor supporting load commissioning documentation |  |  |  |

| STAGE 4 NORMAL OPERATION VOLTAGE, CURRENT & TEMPERATURE |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 240 VAC 415 VAC Other _____________ _______________________________ |  |  |  |  |  |  |
| Test Location: |  |  |  |  |  |  |
| Test Points | Current Result |  |  | Voltage Result |  | Pass/Fail |
| 1ø A | Measured _______ Indicated ________ |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| 3ø R | Measured _______ Indicated ________ |  |  |  |  | Pass Fail |
| 3ø W | Measured _______ Indicated ________ |  |  |  |  | Pass Fail |
| 3ø B | Measured _______ Indicated ________ |  |  |  |  | Pass Fail |
| 3ø R - W |  |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| 3ø R - B |  |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| 3ø W - B |  |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| 3ø R - N |  |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| 3ø W - N |  |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| 3ø B - N |  |  |  | Measured _______ Indicated ________ |  | Pass Fail |
| TEMPERATURE MEASUREMENT |  |  |  |  |  | Pass Fail |
| DB | Ambient __________________ |  |  | Infra-Red Measured _______________ |  | Pass Fail |
|  | Voltage and Current draw within design or within name plate acceptable limits Y N |  |  |  |  |  |

| STAGE 4 NORMAL OPERATION AUXILLIARY VOLTAGE, CURRENT & TEMPERATURE |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 240 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: |  |  |  |  |  |  |
| Test Points | Current Result |  |  | Voltage Result |  | Pass/Fail |
| 1ø A | Measured _______ Indicated ________ |  |  | Measured _______ Indicated ________ |  | Pass Fail |
|  | Voltage and Current draw within design or within name plate acceptable limits Y N |  |  |  |  |  |

| Attach supporting documentation, including SCADA screen shots and IR images. |  |  |
| --- | --- | --- |
| Item | Document Name/ Type | Appended to ITR (Initial) |

| VENDOR LOAD COMMISSIONING RECORDS N/A |  |  |
| --- | --- | --- |
| As a minimum all supporting test documentation shall reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |
| Item | Vendor Document Name / Type | Appended to ITR (Initial) |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |