| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and Schematic. |  |  |  |
|  | Confirm panel location, installation and orientation are correct as per the design drawings. |  |  |  |
|  | Confirm mechanical operation is unimpeded, IP rating is not compromised, and the equipment is free from damage, rust, contamination and debris internally and externally. |  |  |  |
|  | Confirm that all labels are correct. |  |  |  |
|  | Confirm panel earthing is of correct size, connected and tightened, all earthing arrangements are in place and labelled correctly as per applicable drawings. |  |  |  |
|  | Confirm door seal is secure and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm gland plate is connected to earth. |  |  |  |
|  | Confirm gland plate is secure and gasket in place. |  |  |  |
|  | Confirm glands are installed as per manufacturer’s recommendations and unused cable entries are plugged. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm wiring looms are neat with ducting covers fitted. |  |  |  |
|  | Confirm control wiring has correct colour coding, sizing and is ferruled correctly. |  |  |  |
|  | Confirm terminal rails are secure and terminal numbering is in place and correct. |  |  |  |
|  | Confirm rating, continuity and mechanical operation of Main Isolator. |  |  |  |
|  | Confirm rating, continuity and mechanical operation of MCBs. |  |  |  |
|  | Confirm all external control selector switches, stop buttons and push buttons are correctly mounted, sealed and operate full their full range of motion. |  |  |  |
|  | Confirm indicators and push buttons are of the correct colours. |  |  |  |
|  | Where applicable, confirm sun covers are installed and mounted correctly. |  |  |  |
|  | Perform continuity test between main earth and all internal earthed equipment, devices, enclosure and other conductive parts with results recorded below: |  |  |  |

| CONTINUITY, PHASING & EARTH CONTINUITY |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R |  | Ω |
| W-W | N/A | Ω |
| B-B | N/A | Ω |
| N-N |  | Ω |
| E-E |  | Ω |
| E-Gland Plate |  | Ω |
| E-Door |  | Ω |
| EP-Bond |  | Ω |
| Point to Point Confirmed Y N | Continuity Compliance Pass Fail | Isolator Operation Confirmed Y N |

| INSULATION RESISTANCE TEST (Control Panel – If applicable) N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  |  | Calibration Due Date: |  |  |  |  |  |
| Note: IR tests to meet the requirements of AS3000:2018 may be conducted on all electrical circuits using only a suitable test voltage for which the equipment or device is capable of withstanding. IR tests will not be conducted on communications or data circuits where there is of damaging internal sensitive electronic circuits. |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Point | R to W | R to B |  | W to B | R to N | W to N |  | B to N |  | RWB to E |  | N to E |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC |  | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ | MΩ | MΩ |  | MΩ |  | MΩ |  | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  | Pass |  | Fail |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |