| Tag No. «Name» - «Description» |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |
| Drawing No. |  | «DocumentList» |  | Task No. | «TaskName» |  |
| Additional Information: |  | «Comments» |  |  |  |  |
| EQUIPMENT DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | VA Rating |  |  |  |
| Type |  |  | Highest Voltage |  |  |  |
| Serial No |  |  | Rated Short Time Thermal Current |  |  |  |
| Accuracy Class |  |  | Insulation Class |  |  |  |
| Ratio |  |  | Other |  |  |  |
| Frequency |  |  |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| PRE-REQUISITE |  |  |  |  |
|  | Confirm availability of CT data sheet, single line, layout, general arrangement and schematic drawings are available. |  |  |  |
|  | Confirm Manufactures applicable Type and Routine Tests as per the data sheet and applicable standards have been completed and evidence provided. |  |  |  |
| PHYSICAL, INSTALLATION AND EQUIPMENT CHECKS |  |  |  |  |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. |  |  |  |
|  | Confirm the CT Class, Rating & Ratio are as per the single Line/ schematic |  |  |  |
|  | Confirm location is correct the CT is firmly mounted, physically aligned with adequate clearances as per design. |  |  |  |
|  | Confirm CT has been installed as per polarity direction indication. |  |  |  |
|  | Confirm all equipment is free from mechanical damage. |  |  |  |
|  | Confirm control wiring between the CT and the relay is correct as per schematic drawings. |  |  |  |
|  | Confirm CT Terminals, terminal blocks and CT shorting links are correctly labelled and ferruled. |  |  |  |
|  | Confirm wiring looms are secure neat and tidy. |  |  |  |
|  | Confirm wiring looms for segregation and separation where applicable. |  |  |  |
|  | Confirm that terminations are clean, tight and that all lugs are crimped correctly and check that all nuts, washers and spring washes are in place. |  |  |  |
|  | Confirm that equipment earthing is correct, terminations are clean and tight. |  |  |  |
|  | Confirm there is only one single point of earthing on each CT secondary. |  |  |  |
| ##### Note: Refer to SS-E115 for Test Durations and Test Pass Fail Criteria. For CT’s with more than one secondary winding, test reports shall be generated for each winding. |  |  |  |  |  |

| ##### TRANSFORMER POLARITY TEST – (Only Required if Factory Test Results Not Available) N/A |  |  |  |
| --- | --- | --- | --- |
| ##### Test Equipment: |  | ##### Serial No. | ##### Calibration Date: |
|  | Carry out the Transformer Polarity Tests as per the type of the CT and attach the test report. |  |  |

| ##### CT INSULATION TEST – (Only Required if Factory Test Results Not Available) N/A |  |  |  |
| --- | --- | --- | --- |
| Test Equipment: |  | Serial No. | Calibration Date: |
|  | Carry out the Insulation Resistance Tests as per the type of the CT and attach the test report. |  |  |

| ##### TRANSFORMER RATIO TESTS – (Only Required if Factory Test Results Not Available) N/A |  |  |  |
| --- | --- | --- | --- |
| Test Equipment: |  | Serial No. | Calibration Date: |
|  | Carry out the Ratio Tests as per the type of the CT and attach the test report. |  |  |

| ##### CT KNEE POINT TESTS – (Only Required if Factory Test Results Not Available) N/A |  |  |  |
| --- | --- | --- | --- |
| Test Equipment: |  | Serial No. | Calibration Date: |
|  | Carry out the Knee Point Test and attach the test report. Knee Point Voltage and Current must be identified on the report. |  |  |

| COMPLETION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm CTs are discharged to Earth. |  |  |  |
|  | Confirm CT Slide Links are closed, all terminations are reinstated and are tight and secure. |  |  |  |
|  | Replace all covers and confirm the CT safe and ready for energisation and function testing. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |