| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

Decontactors, Large J boxes & Field Isolators

Note: This ITR is only suitable for Field Decontactors, Large J Boxes such as cable gauge change enclosures and mechanically operated field Isolators. The ITR is not intended for small non-metallic mass-produced junction boxes such as Posi-box

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm panel location, installation and orientation are correct as per the design drawings. |  |  |  |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. |  |  |  |
|  | Confirm mechanical operation is unimpeded, IP rating is not compromised, and the Junction Box is free from damage, rust, contamination and debris internally and externally. |  |  |  |
|  | Confirm JB earthing connected and tightened, all earthing arrangements are in place and labelled correctly as per applicable drawings. |  |  |  |
|  | Confirm gland plate is secure, earthed and gasket in place. |  |  |  |
|  | Confirm glands are installed as per manufacturer’s recommendations and unused cable entries are plugged. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm Wiring looms are neat and all duct covers are installed. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm terminal rails are secure and terminal numbering is in place and correct. |  |  |  |
|  | Confirm there is one wire per terminal. |  |  |  |
|  | Where applicable, confirm sun or protective covers are installed and mounted correctly. |  |  |  |
|  | Confirm continuity of phases and between main earth and all internal earthed equipment, devices, enclosure and other conductive parts. |  |  |  |
|  | Complete J-Box and Gauge Change boxes IR tests of internal hardware and insulated stand-offs. |  |  |  |
|  | For De-contactors, confirm plug and socket phasing is maintained across the connection. |  |  |  |

| INSULATION RESISTANCE TEST (for LV J-Box or Gauge Change Box) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  |  | Calibration Due Date: |  |  |  |  |  |
| Note: IR tests to meet the requirements of AS3000:2018 may be conducted on all electrical circuits using only a suitable test voltage for which the equipment or device is capable of withstanding. IR tests will not be conducted on communications or data circuits where there is of damaging internal sensitive electronic circuits. For off-the-shelf junction boxes such as "Posibox" and plastic double insulated decontactors, IR checks are not required. IR checks associated with Metal decontactors are required. |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Point | R to W | R to B |  | W to B | R to N | W to N |  | B to N |  | RWB to E |  | N to E |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC |  | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ | MΩ | MΩ |  | MΩ |  | MΩ |  | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  | Pass |  | Fail |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm enclosure integrity and Bus, Cable, Cable Lug or Lug Bolt separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm equipment is left clean, free from debris and test tools. |  |  |  |
|  | Reconnect all the cables back, replace covers and confirm equipment is left safe ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |  |
| Signature: |  | Signature: |  | Signature: |  |  |
| Name: |  | Name: |  | Name: |  |  |
| EW Licence No.: |  | Title: |  | Title: |  |  |
| Date: |  | Date: |  | Date: |  |  |