| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate Details as per Datasheet. |  |  |  |
|  | Confirm mounting is firm, IP rating not compromised and not subject to vibration. |  |  |  |
|  | Confirm labelling is correct. |  |  |  |
|  | Confirm location and orientation is correct. |  |  |  |
|  | Confirm surface finish is undamaged (no paint chips). |  |  |  |
|  | Confirm door seal is secure and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm gland plate is earthed. |  |  |  |
|  | Confirm gland plate is secure and gasket in place. |  |  |  |
|  | Confirm glands are installed as per manufacturers recommendations and unused cable entries plugged. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm ducting covers are fitted. |  |  |  |
|  | Confirm wiring is consistent with design drawings. |  |  |  |
|  | Confirm that the circuit schedule is correct, neat and located inside the DB with neutral numbers marked on circuits. |  |  |  |
|  | Confirm terminal rails are secure and terminal numbering is in place and correct. |  |  |  |
|  | Confirm terminals are firmly tightened with one core per terminal. |  |  |  |
|  | Confirm rating, continuity and mechanical operation of the Main Isolator. |  |  |  |
|  | Confirm rating, continuity and mechanical operation of sub-circuit protective devices (CBs and RCDs). |  |  |  |
|  | Confirm Main Isolator, CBs and RCDs can be locked in the OFF position. |  |  |  |
|  | Confirm contactors and selector switches for correct installation, mechanical operation and damage. |  |  |  |
|  | Confirm that busbars are insulated and phase indication has been fitted where required. |  |  |  |
|  | Confirm any modifications correctly Red Lined and As Constructed drawings submitted. |  |  |  |

| CONTINUITY, PHASING & EARTH / MEN N-E TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Resistance | Remarks |
| R-R | Ω |  |
| W-W | Ω |  |
| B-B | Ω |  |
| N-N | Ω |  |
| MEN-E | Ω |  |
| E-Gland Plate | Ω |  |
| E-Door | Ω |  |
| Point to Point Confirmed Y N | Continuity Compliance Pass Fail | Isolator Operation Confirmed Y N |

| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  | Calibration Due Date: |  |  |
| Test Point | R to W | R to B | W to B | R to N | W to N | B to N | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm enclosure surround and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |