| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cable Type: | «CableType» |  | Cable Rating: | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm that cable is identified correctly at both ends as per the cable schedule and goes to correct location. |  |  |  |
|  | Confirm connections are tight and free from corrosion. |  |  |  |
|  | Confirm cable size and type is correct as per the cable schedule. |  |  |  |
|  | Confirm cable support and enclosure systems are satisfactory and secure. |  |  |  |
|  | Confirm cable bending radius has not been exceeded. |  |  |  |
| Note: All tests below must be supported by an attached grid and stake layout drawing. If a design drawing is not available then a suitable sketch must be provided to support the location and identification of test points: Sketch shall include the following: 1. Horizontal earth grid conductors. 2. Locations of exothermic or crimped joints on the horizontal conductors. 3. Location of all equipotential joints to surface equipment. 4. Locations of all earth stakes. |  |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Photo ID |  | Description | Taken By |

| EARTH CONTINUITY TEST |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: | Calibration Date: |  |  |
| Running Earth Y N |  | Structural Earth Y N | Earth Mat/Grid Y N |  |  |
| Test | Cable End 1 | Cable End 2 | Resistance |  |  |
| Test 1 |  |  | Ω |  |  |
| Test 2 |  |  | Ω |  |  |
| Test 3 |  |  | Ω |  |  |
| Test 4 |  |  | Ω |  |  |
| Test 5 |  |  | Ω |  |  |
| Test 6 |  |  | Ω |  |  |
| Test 7 |  |  | Ω |  |  |
| Test 8 |  |  | Ω |  |  |
| Test 9 |  |  | Ω |  |  |
| Test 10 |  |  | Ω |  |  |
| Test 11 |  |  | Ω |  |  |
| Test 12 |  |  | Ω |  |  |
| Acceptance criteria – Phasing/Point to Point/Continuity resistance: - Conductor ID/Phasing/Line identification and marking is consistent from point of supply to point of destination is consistent throughout the installation under test in accordance with the design. - For cable: Continuity resistance results are within manufacturer’s recommendations for cable cross sectional area and cable length. For equipotential bonding conductor and equipotential bond total resistance shall not exceed 0.5 Ω - Any outlier or inconsistent results outside of the mean are considered a failed result requiring further investigation. |  |  |  |  |  |
| Continuity Compliance |  |  |  | Pass | Fail |
| Point to Point Confirmed |  |  |  | Y | N |

| DUCTOR TESTS - GRID JOINTS Switchyard Earth Grid Structural Earthing Sample Only Applicable to Earth Grids ≥33kV otherwise completed as directed on a sample basis for buried structural earthing N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Instrument Used: |  |  |  |  |
| Test Equipment: |  | Serial No.: |  | Calibration Date: |
| Reference Point : |  |  | Closest Main Earth |  |

| Test Point ID | Test Current (A) | Resistance (mΩ) (<100 mΩ) | Test Point ID | Test Current (A) | Resistance (mΩ) (<100 mΩ) |
| --- | --- | --- | --- | --- | --- |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Where applicable, confirm all cable ends are suitably capped and protected from the ingress of moisture and environmental elements. |  |  |  |
|  | Confirm cables are suitably protected, supported and windrowed where applicable to ensure segregation between personal and vehicular traffic. |  |  |  |
|  | Confirm conduit entries are suitability covered/filled. |  |  |  |
|  | Confirm pit covers are replaced. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |