| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Earth Bars conform to specification and drawings. |  |  |  |
|  | Confirm Earth Cable connections are installed, torqued to spec, secured to the Earth Bar and free from corrosion and damage. |  |  |  |
|  | Confirm that the Earth electrodes are properly installed as per design and connected to the earth system by the earth conductors. |  |  |  |
|  | Confirm that all earth cables are the correct size in accordance with the cable schedule. |  |  |  |
|  | Confirm Earth Cables are correctly labelled as per design drawings. |  |  |  |
|  | Confirm that the Earth Pits are properly installed, level with finish surface, free of backfill and access to the earth electrodes is possible and the earth pit lids are in good condition. |  |  |  |
|  | Confirm that earth electrode connections are clean, tight, secure and coated with protective coating. |  |  |  |
|  | For drilled earth rods, confirm depth and enhancing compounds are as per design. |  |  |  |
| Note: All tests below must be supported by an attached grid and stake layout drawing. If a design drawing is not available, then a suitable sketch must be provided to support the location and identification of test points: Sketch shall include the following: 1. Horizontal earth grid conductors. 2. Locations of exothermic or crimped joints on the horizontal conductors. 3. Location of all equipotential joints to surface equipment. 4. Locations of all earth stakes. Refer to SS-273 for Test Criteria |  |  |  |  |

| EARTH GRID EARTH CONTINUITY (All Grids & Stakes) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Instrument Used: |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No.: |  |  | Calibration Date: |  |
| Attach layout drawing to indicate test points |  |  |  |  |  |  |  |  |
| Test Point A ID | Test Point B ID |  | Resistance (Ω) |  | Test Point A ID | Test Point B ID |  | Resistance (Ω) |
| Point to Point Confirmed Y N |  |  |  |  | Continuity Compliance Pass Fail |  |  |  |

| EARTH LOOP IMPEDANCE (CLAMP ON TEST) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Instrument Used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  |  |  |  |  | Serial No.: |  |  |  |  |  |  |  | Calibration Date: |  |  |  |
| Attach layout drawing to indicate test points |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test No. |  |  | Test Point |  |  |  |  |  |  |  |  |  |  | Resistance (Ω) |  |  |  |  |  |
| Results Acceptable Pass Fail |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CONTACT RESISTANCE (DUCTOR) - ALL GRID JOINTS AND CONNECTIONS TO STRUCTURES Substation/Switchyard Earth Grid Structural Earthing Sample Only Applicable to Earth Grids ≥33kV otherwise completed as directed on a sample basis for buried structural earthing N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Instrument Used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  |  |  |  |  | Serial No.: |  |  |  |  |  |  |  |  |  | Calibration Date: |  |
| Refer to SS-273 for Test Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Point : |  |  |  |  |  |  |  |  | Closest Main Earth |  |  |  |  |  |  |  |  |  |  |
| Test Point ID |  | Test Current (A) |  |  |  | Resistance (mΩ) (<100 mΩ) |  |  | Test Point ID |  |  |  | Test Current (A) |  |  |  |  | Resistance (mΩ) (<100 mΩ) |  |
| CURRENT DISTRIBUTION – INJECTION TESTING (Switchyards and Substations Only) N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment Used |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Instrument |  |  |  |  |  |  | Model |  |  |  | Serial Number |  |  |  |  |  | Calibration Date |  |  |
| Injection Current |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Injection Frequency (Hz) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Time | Location/ Conductor |  |  |  | Ammeter Reading (amps) |  | Ammeter Reading/ Number of turns |  |  | Time |  | Location/ Conductor |  |  | Ammeter Reading (amps) |  |  |  | Ammeter Reading/ Number of turns |
|  | Injection current at start of test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Injection current at finish of test |  |  |  |  |  |  |  |

| VOLTAGE GRADIENT/EPR/IMPEDANCE (Switchyards and Substations Only) N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment Used |  |  |  |  |  |  |  |  |  |  |  |  |
| Instrument |  |  | Model |  |  |  | Serial Number |  |  |  | Calibration Date |  |
| VOLTAGE GRADIENT MEASUREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |
| Injection Frequency (Hz) |  |  |  |  |  |  |  |  |  |  |  |  |
| Time | Distance from earthing grid under test to Voltage Spike (metres) |  |  | Injection Current (Amps) (must be >1A) |  | Measured Voltage (at offset frequency) between voltage spike and: |  |  |  |  |  |  |
|  |  |  |  |  |  | Earthing grid under test Volts |  |  | Remote earth (Powerlink only) Volts |  |  |  |
| EARTH POTENTIAL RISE MEASUREMENTS (at “plateau” of voltage gradient) N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| Attach layout drawing to indicate test points: |  |  |  |  |  |  |  |  |  |  |  |  |
| Time | Distance from earthing grid under test to Voltage Spike (metres) |  |  | Injection Current (Amps) | Measured Voltage between earthing grid under test and voltage spike |  |  |  |  |  |  |  |
|  |  |  |  |  | Measured Voltage at Offset Freq. (V) |  |  | RMS Measured Voltage (V) |  | Standing Voltage at Offset Freq. (V) |  | RMS Standing Voltage (V) |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker or Engineer. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No/ Test Engineer: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |