| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labeling is as per GA and schematic. |  |  |  |
|  | Confirm device location, installation and orientation is correct as per the design drawings. |  |  |  |
|  | Confirm device mechanical operation is unimpeded, IP rating is not compromised, and the device is free from damage, rust, contamination and debris internally and externally. |  |  |  |
|  | Confirm that all labels are correct. |  |  |  |
|  | Confirm device earthing is of correct size, connected and tightened, all earthing arrangements are in place and labelled correctly as per applicable drawings. |  |  |  |
|  | Confirm Glands are installed as per manufacturer’s recommendations and unused cable entries are plugged. |  |  |  |
|  | Confirm all gaskets and seals are intact. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm Wiring is as per with design drawings. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare |  |  |  |
|  | Perform a point to point test and confirm continuity of phases and between main earth and all internal earthed equipment, devices, enclosure and other conductive parts. |  |  |  |
|  | Confirm IR tests of internal hardware and insulated stand-offs – as applicable. |  |  |  |
|  | Attach any tests specific to the type of the equipment and attach the results. |  |  |  |

| PHASING & CONTINUITY TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Connections | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R |  | Ω |
| W-W | N/A | Ω |
| B-B | N/A | Ω |
| N-N |  | Ω |
| E-E |  | Ω |
| E-Gland Plate | N/A | Ω |
| E-Enclosure Lid |  | Ω |
|  | Phase Point to Point Confirmed Y N | Continuity Confirmed Pass Fail |

| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. |  |  | Calibration Due Date: |  |  |
| Note: IR tests to meet the requirements of AS3000:2018 may be conducted on all electrical circuits using only a suitable test voltage for which the equipment or device is capable of withstanding. IR tests will not be conducted on communications or data circuits where there is of damaging internal sensitive electronic circuits. |  |  |  |  |  |  |  |  |
| Test Point | R to W | R to B | W to B | R to N | W to N | B to N | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm equipment is left clean, free from debris and test tools. |  |  |  |
|  | Reinstate, replace covers and confirm equipment is left safe ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |