| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. |  |  |  |
|  | Confirm device location, installation and orientation is correct as per the design drawings. |  |  |  |
|  | Confirm equipment is free from damage and debris internally and externally. |  |  |  |
|  | Confirm IP rating is correct. |  |  |  |
|  | Confirm all gaskets and seals are intact. |  |  |  |
|  | Confirm gland plate is secure and gasket in place. |  |  |  |
|  | Confirm glands are installed as per manufacturer’s recommendations and unused cable entries are plugged. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm wiring is as per design drawings. |  |  |  |
|  | Confirm mechanical operation of all control devices such as push buttons, stop buttons and switches. |  |  |  |
|  | As applicable, complete the table below for Continuity and Insulation Resistance. |  |  |  |
|  | If applicable, complete the Contact Resistance and Bolt Torque tables below for internal hardware terminations. |  |  |  |

| PHASING & CONTINUITY TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Connections | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R |  | Ω |
| W-W | N/A | Ω |
| B-B | N/A | Ω |
| N-N |  | Ω |
| E-E |  | Ω |
| E-Gland Plate |  | Ω |
| E-Door |  | Ω |
|  | Phase Point to Point Confirmed Y N | Continuity Confirmed Pass Fail |

| INSULATION RESISTANCE TEST (Single Phase) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  |  | Calibration Date: |  |  |  |
| Note: IR tests to meet the requirements of AS3000:2018 may be conducted on all electrical circuits using only a suitable test voltage for which the equipment or device is capable of withstanding. IR tests will not be conducted on communications or data circuits where there is of damaging internal sensitive electronic circuits. |  |  |  |  |  |  |  |  |
| Test Point | R to E |  | R to N | N to E |  |  |  |  |
| Test Voltage | 500 VDC |  | 500 VDC | 500 VDC |  |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  | MΩ | MΩ |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |  |

| INSULATION RESISTANCE TEST (Three Phase) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  | Calibration Due Date: |  |  |
| Note: IR tests to meet the requirements of AS3000:2018 may be conducted on all electrical circuits using only a suitable test voltage for which the equipment or device is capable of withstanding. IR tests will not be conducted on communications or data circuits where there is of damaging internal sensitive electronic circuits. |  |  |  |  |  |  |  |  |
| Test Point | R to W | R to B | W to B | R to N | W to N | B to N | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| CONTACT RESISTANCE N/A |  |  |  |  | BOLT TORQUE N/A |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |
| Torque Wrench Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |
| Test Point | Micro Ohms | Test Point | Micro Ohms | Point of supply |  | Torque Nm |  | Point of destination | Torque Nm |
|  | µΩ |  | µΩ |  |  | Nm |  |  | Nm |
|  | µΩ |  | µΩ |  |  | Nm |  |  | Nm |
|  | µΩ |  | µΩ |  |  | Nm |  |  | Nm |
|  | µΩ |  | µΩ |  |  | Nm |  |  | Nm |
|  | µΩ |  | µΩ |  |  | Nm |  |  | Nm |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm equipment surround - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm Equipment is left safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |