| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer. |  |  |  | «ManufacturerName» |  | Model No. |  | «OEMPartNumber» |  |  |  |
| Field to record Serial No. |  |  |  | «SerialNumber» |  |  |  |  |  |  |  |
| Drawing No. |  |  |  | «DocumentList» |  | Task No. |  | «TaskName» |  |  |  |
| Additional Information: |  |  |  | «Comments» |  |  |  |  |  |  |  |
| ALTERNATOR DATA |  |  |  |  |  |  |  |  |  |  |  |
| Make |  |  |  | Alternator Efficiency % |  |  |  |  |  |  |
| Model |  |  |  | Power Factor Rating (pf) |  |  |  |  |  |  |
| Serial Number |  |  |  | ENGINE DATA |  |  |  |  |  |  |
| Output (kW) |  |  |  | Make |  |  |  |  |  |  |
| Output kVA |  |  |  | Model |  |  |  |  |  |  |
| RPM |  |  |  | Engine Number |  |  |  |  |  |  |
| Frequency (Hz) |  |  |  | HP(kW) / RPM |  | / |  |  |  |  |
| Voltage (V) |  |  |  | Serial Number |  |  |  |  |  |  |
| Current (A) |  |  |  | Cooling Type |  |  |  |  |  |  |
| Phase |  |  |  | No. of Cylinders |  |  |  |  |  |  |
| Note: This ITR is unsuitable for use for generation systems requiring grid connect or generators in parallel. It is intended for single generator LV applications only. EPR Consideration must be given to generator MEN connection or existing MEN interaction with connected infrastructure such as switchboards or motor control centres. |  |  |  |  |  |  |  |  |  |  |
| Item |  | Description |  |  |  |  |  |  | OK | N/A | Punch |
|  |  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and Schematic. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm battery terminals are free from corrosion and battery terminal dielectric grease has been applied. |  |  |  |  |  |  |  |  |  |
|  |  | Verify electrolyte level in batteries is sufficient, add manufacturer specified electrolyte if required. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all mounting bolts are tight and secure. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm overall enclosure is in sound condition with no visible mechanical damage. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm access is clear, hatches and doors are unobstructed, open/ close and seal correctly. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm enclosed areas are clean and free of dust and debris (including cable ties, wire offcuts, dirt and rubbish). |  |  |  |  |  |  |  |  |  |
|  |  | Confirm direction and phase rotation is clearly marked. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm ventilation (intake and exhaust) paths are clear and not obstructed. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm bunding is free of debris or objects that may impede bunding volume capacity. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all equipment carries the correct circuit identification. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all electrical connections are correct as per design, tight and secure. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm gland plates are earthed and accessible. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm gaskets and seals are not damaged. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm cable protective measures (kick plates) are installed. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all cable entry covers and terminal boxes are clean and secure. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all Earth cables are sized correctly as per design or application. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all earth cables are correctly terminated as per wiring schematic. |  |  |  |  |  |  |  |  |  |
|  |  | Attach sketch or design drawing for MEN location and Earth Stake requirements. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm MEN link is installed in correct location as per design specification: |  |  |  |  |  |  |  |  |  |
|  |  | Note switchboard location of MEN: |  |  |  |  |  |  |  |  |  |
|  |  | Perform continuity, phase checking and insulation resistance test and record results below: |  |  |  |  |  |  |  |  |  |

| CONTINUITY, PHASING & EARTH / MEN N-E TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  |  |  | Calibration Date: |  |  |  |  |
| Test Points |  |  | Point to Point Check (Initial Pass/Fail) |  |  |  |  | Continuity Check – Result Ω |  |  |  |  |
| R-R |  |  |  |  |  |  |  | Ω |  |  |  |  |
| W-W |  |  |  |  |  |  |  | Ω |  |  |  |  |
| B-B |  |  |  |  |  |  |  | Ω |  |  |  |  |
| N-N |  |  |  |  |  |  |  | Ω |  |  |  |  |
| MEN-E |  |  |  |  |  |  |  | Ω |  |  |  |  |
|  |  |  | Phase Point to Point Confirmed Y N |  |  |  |  | Continuity Compliance Pass Fail |  |  |  |  |
| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment |  |  |  |  | Serial No. |  |  |  |  | Calibration Due Date: |  |  |
| Test Point | R to W | R to B |  | W to B |  | R to N | W to N |  | B to N |  | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |
| Insulation Resistance Compliance |  |  |  |  |  |  |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm enclosure surround and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |