| Tag No. «Name» - «Description» |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |
| Drawing No. |  | «DocumentList» |  | Task No. |  | «TaskName» |
| Additional Information: |  | «Comments» |  |  |  |  |
| PANEL/ MODULE PROTECTION RELAY DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | PDP/MCC No. |  |  |  |
| Type/Model |  |  | Panel/Tier No |  |  |  |
| PANEL/MODULE CIRCUIT BREAKER / INCOMER / FEEDER / EQUIPMENT DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | Size (A) |  |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS & PHYSICAL CHECKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR Task Asset and Asset Tag Identification. |  |  |  |
|  | Confirm As-Constructed Red-Line Drawings available. |  |  |  |
|  | Confirm Manufactures applicable Function, Protection and Routine Tests as per the data sheet, manufacturers ITP and applicable standards have been completed and evidence provided. |  |  |  |
|  | Confirm downstream Circuit Breaker(s)/ Isolator(s) are Open prior to energisation. |  |  |  |
|  | Confirm all downstream LV final sub-circuit or auxiliary circuits not part of this energisation are under isolation permit, disconnected, identified and made safe (if applicable). |  |  |  |
|  | Confirm all downstream ELV auxiliary circuits not part of this energisation are disconnected, identified and made safe (If Applicable). |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and check of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all ELV & LV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Confirm all internal covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |

| LV & ELV AUXILIARY CONTROL SUPPLY ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Energise or confirm energisation of auxiliary control supplies. |  |  |  |
|  | Complete the Panel/ Module Auxiliary Control Voltage Table(s) below for each Aux control supply. |  |  |  |

| AUX 1 - LV & ELV CONTROL AUXILLIARY SUPPLY – POLARITY & VOLTAGE |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No.: | Calibration Date: |  |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 110 VAC 240 VAC Other ___________ |  |  |  |  |  |  |
| Test Location: |  |  |  |  |  |  |
| Test Points |  |  | Voltage Result |  |  | Remarks |
| A - N | N/A Polarity OK |  | Measured _______ Indicated ________ |  |  | Pass Fail |
| A - E | N/A Polarity OK |  | Measured _______ |  |  | Pass Fail |
| N - E | N/A Polarity OK |  | Measured _______ |  |  | Pass Fail |
|  |  |  | Polarity & Voltage Acceptable Y N |  |  |  |

| AUX 2 - LV & ELV CONTROL AUXILLIARY SUPPLY – POLARITY & VOLTAGE N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 110 VAC 240 VAC Other ___________ |  |  |  |  |
| Test Location: |  |  |  |  |
| Test Points |  |  | Voltage Result | Remarks |
| A - N | N/A Polarity OK |  | Measured _______ Indicated ________ | Pass Fail |
| A - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
| N - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
|  |  |  | Polarity & Voltage Acceptable Y N |  |

| AUX 3 - LV & ELV CONTROL AUXILLIARY SUPPLY – POLARITY & VOLTAGE N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 110 VAC 240 VAC Other ___________ |  |  |  |  |
| Test Location: |  |  |  |  |
| Test Points |  |  | Voltage Result | Remarks |
| A - N | N/A Polarity OK |  | Measured _______ Indicated ________ | Pass Fail |
| A - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
| N - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
|  |  |  | Polarity & Voltage Acceptable Y N |  |

| AUX 4 - LV & ELV CONTROL AUXILLIARY SUPPLY – POLARITY & VOLTAGE N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 110 VAC 240 VAC Other ___________ |  |  |  |  |
| Test Location: |  |  |  |  |
| Test Points |  |  | Voltage Result | Remarks |
| A - N | N/A Polarity OK |  | Measured _______ Indicated ________ | Pass Fail |
| A - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
| N - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
|  |  |  | Polarity & Voltage Acceptable Y N |  |

| AUX 5 - LV & ELV CONTROL AUXILLIARY SUPPLY – POLARITY & VOLTAGE N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 110 VAC 240 VAC Other ___________ |  |  |  |  |
| Test Location: |  |  |  |  |
| Test Points |  |  | Voltage Result | Remarks |
| A - N | N/A Polarity OK |  | Measured _______ Indicated ________ | Pass Fail |
| A - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
| N - E | N/A Polarity OK |  | Measured _______ | Pass Fail |
|  |  |  | Polarity & Voltage Acceptable Y N |  |

| AUXILIARY LIGHTING & HEATER SUPPLY ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | If applicable, energise Panel/ Module Lighting & Heater supplies. |  |  |  |
|  | Complete the Auxiliary Voltage Lighting & Heater Supply Table below. |  |  |  |
|  | Complete the Auxiliary Voltage Lighting & Heater Supply Current Draw Table below. |  |  |  |

| LOW VOLTAGE AUXILIARY LIGHTING & HEATER POLARITY & VOLTAGE N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| Heater Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |
| Heater Test Location: |  | N/A |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  | Remarks |
| A - N | N/A Polarity OK | Measured _______ Indicated _______ |  |  | Pass Fail |
| A - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| Lighting Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |
| Lighting Test Location: |  | N/A |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  | Remarks |
| A - N | N/A Polarity OK | Measured _______ Indicated _______ |  |  | Pass Fail |
| A - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
|  |  | Polarity, Voltage & Phase Indication Acceptable Y N |  |  |  |

| LOW VOLTAGE AUXILIARY LIGHTING & HEATER SUPPLY – STAGE 2 CURRENT DRAW N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: | Calibration Date: |  |  |
| Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |
| Heater Test Location: |  | N/A |  |  |  |
| Test Points |  | Current Draw | Remarks |  |  |
| 1ø - A | N/A | Measured _______A |  |  |  |
| Lighting Test Location: |  | N/A |  |  |  |
| Test Points |  | Current Draw | Remarks |  |  |
| 1ø - A | N/A | Measured _______A |  |  |
|  |  | Current draw within design or within name plate acceptable limits Y N |  |  |  |

| STAGE 2 POST AUXILIARY ENERGISATION FUNCTION & PHYSICAL VERIFICATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm PLC & SCADA communication - healthy status and indication. |  |  |  |
|  | Confirm protection relay communication - healthy status and indication. |  |  |  |
|  | Confirm Fortress key mechanical interlock system(s) and system methodology operates as per design. |  |  |  |
|  | Manually operate the incomer, feeder circuit breaker to confirm Open/ Close, In-service & Test function is as per design. |  |  |  |
|  | If applicable, manually operate the Isolator to confirm Open/ Close functionality and interlocking is as per design. |  |  |  |
|  | If applicable, manually operate the Earth switch to confirm Open/ Close functionality and interlocking is as per design. |  |  |  |
|  | If applicable, confirm manual racking and spring charge mechanisms operate as per design. |  |  |  |
|  | Confirm mechanical interlocking and position indication is operating as per design. |  |  |  |
|  | Confirm electrical interlocking and position indication is operating as per design. |  |  |  |
|  | Confirm panel/ module status indicators are operating as per design. |  |  |  |
|  | If applicable, confirm local/manual racking and spring motor charge mechanisms operate as per design. |  |  |  |
|  | Remotely operate the isolator, incomer, feeder to confirm Open/ Close, In-service & Test function is as per design. |  |  |  |
|  | If applicable, local pendant operate the isolator, incomer or feeder to confirm Open/ Close, In-service & Test function is as per design. |  |  |  |
|  | Confirm all Safety Related Control Function (SRCF) PLC I/O - status, indication and values are in accordance with functionality and design. |  |  |  |
|  | Confirm gas charge indicator and gas charge trip/ lockout alarm function. |  |  |  |
|  | Confirm all SCADA - status, indication and values are in accordance with functionality and design. |  |  |  |
|  | Confirm low volt shut down relay & I/O trip permissives are operating as per design (if applicable). |  |  |  |
|  | Confirm fire shut down relay & I/O trip permissives are operating as per design (if applicable). |  |  |  |
|  | Carry out main incomer/ feeder/ circuit breaker – trip & close coil functional trip and trip timing tests and record the results in the table below. |  |  |  |

| CLOSING & TRIP COIL TESTS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Only Required if Factory Test Results Not Available N/A |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No.: |  | Calibration Date: |  |
| Test Coils | Nominal Voltage | Operating Voltage |  | Resistance (Ω) |  | Remarks |
| CLOSING 1 |  |  |  | Ω |  | N/A |
| CLOSING 2 |  |  |  | Ω |  | N/A |
| TRIP 1 |  |  |  | Ω |  | N/A |
| TRIP 2 |  |  |  | Ω |  | N/A |
| UNDERVOLTAGE |  |  |  | Ω |  | N/A |
| Other: |  |  |  | Ω |  | N/A |
|  |  | Results are within Manufacturers specifications Y N |  |  |  |  |
| Note: Supporting Documentation: As a minimum all supporting test documentation shall be completed using the installed parameters as per the design and must reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |  |

| TIME TESTS |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (Only Required if Factory Test Results Not Available N/A |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No.: |  | Calibration Date: |  |  |
| Test |  | Time (ms) | Travel Distance (mm) |  | Velocity (m/s) |  |  | N/A |
| OPEN - CLOSE |  |  |  |  |  |  |  | N/A |
| CLOSE - OPEN |  |  |  |  |  |  |  | N/A |
| Record Operation Counter: |  |  |  |  | Record Trip Counter: |  |  |  |
| Note: Supporting Documentation: As a minimum all supporting test documentation shall be completed using the installed parameters as per the design and must reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |  |  |  |
|  |  |  | Results are within Manufacturer’s specifications Y N |  |  |  |  |  |
| Item | CLOSE, TRIP & Timing Supporting Document Name / Type |  |  |  |  |  | Appended to ITR (Initial) |  |

| STAGE 2 SECONDARY INJECTION PROTECTION VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Record the Protection Study document number for the equipment protection parameters, discrimination, grading and relay settings. Protection Study Document Number:_____________________ |  |  |  |
|  | Confirm availability of Protection Relay Data Sheet & Manufacturers IOM Manual. |  |  |  |
|  | Confirm availability of Protection Relay Schematics. |  |  |  |
|  | From the table below select the protection relay ANSI/IECC function codes as referenced in the Protection Study, Data sheet and from the single line and protection diagrams. |  |  |  |

| INCOMER / FEEDER / SWITCH / CIRCUIT BREAKER |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Earth & Neutral |  |  |  | Voltage & Current |  |  |  | Phase & Frequency |  |  |  |
| ANSI | Symbol | Description |  | ANSI | Symbol | Description |  | ANSI | Symbol | Description |  |
| 50 (N or G) | I0>> | Definitive Time Earth Fault Over Current |  | 50 | I>> | Instantaneous Overcurrent |  | 25 | SYNC | Synch or Synch Check Relay |  |
| 51 (N or G) | I0> | Inverse Time Earth Fault Over Current |  | 51 | I> | Inverse Time Over Current |  | 81 | f | Over / Under Frequency Relay |  |
|  | IΔn | Earth Leakage |  | 27 | U< | Under Voltage Relay |  | 79 | 0→1 | Auto Reclose |  |
| 59N | U0> | Neutral Point Displacement Relay |  | 59 | U> | Over Voltage Relay |  |  |  |  |  |
| 67N |  | Directional Earth Fault |  | 68 | I2> | Inrush Current |  |  |  |  |  |
| 67G |  | Ground Directional |  | 87 | ΔI> | Differential Protection |  | Thermal |  |  |  |
|  |  |  |  | 32 |  | Directional Overpower |  | 49F | Ith> | Thermal Prot Cables |  |
|  |  |  |  | 37 |  | Under Power/Under Current |  | 49 (Tor G) |  | Thermal Prot Tx or Generator |  |
|  |  |  |  | 46 |  | Negative Seq Current |  | 26 |  | Over Temperature |  |
|  |  |  |  | 47 |  | Negative Seq Voltage |  |  |  |  |  |
|  |  |  |  | 67 |  | Directional Overcurrent |  |  |  |  |  |
|  |  |  |  | 87L |  | Current Differential |  |  |  |  |  |
|  |  |  |  | 87B |  | BUS Current Differential |  |  |  |  |  |
|  |  |  |  | 87L |  | Segregated Line current differential |  |  |  |  |  |
| Motor External |  |  |  | Motor Internal |  |  |  | Other (Record) |  |  |  |
| ANSI | Symbol | Description |  | ANSI | Symbol | Description |  | ANSI | Symbol | Description |  |
| 38 |  | Bearing Temperature |  | 46 |  | Current Unbalance |  | AFD |  | Arc Flash Detector |  |
| 49P |  | PTC Overtemp |  | 47 |  | Phase Reversal |  | 21 |  | Distance Relay |  |
| 49R |  | RTD Thermal |  | 49T |  | Thermal Model |  | 85 |  | Carrier or Pilot Wire Relay |  |
|  |  |  |  | 66 |  | Starts Per Hour |  | 55 |  | Power Factor Relay |  |
|  |  |  |  | 55 |  | Power Factor |  | 50BF |  | Breaker Failure |  |
|  |  |  |  | 49M |  | Thermal Protection |  |  |  |  |  |
|  |  |  |  | 12 |  | Over Speed |  |  |  |  |  |
|  |  |  |  | 14 |  | Under Speed |  |  |  |  |  |

| Item | Description |  |  | OK | N/A | Punch |
| --- | --- | --- | --- | --- | --- | --- |
|  | Confirm setting/ upload of Protection Relay Function Parameters and trip settings as per the Protection Study. The Manufacturers ITP will stipulate how many points shall be tested for each IDMT element. Pickup and drop off test shall be performed for each definite time element |  |  |  |  |  |
|  | If applicable, for all protection elements identified carry out the required secondary Injection tests. |  |  |  |  |  |
|  | List and attach the test instrument results or Manufacturers FAT test documentation to this ITR. |  |  |  |  |  |
|  | Confirm that all test results measured and expected are within manufacturers operating specifications. |  |  |  |  |  |
|  | Where fitted, confirm protection supervision relay ARC SENSOR instrument Inputs are operating as per design. |  |  |  |  |  |
|  | Confirm all test links have been reinstated and all spare CT cores shorted and earthed as per design in preparation for Primary Injection Testing. |  |  |  |  |  |
| Secondary Injection records as stipulated in the applicable ITP or system commissioning procedure shall be attached as supporting documentation. Note Supporting Documentation: As a minimum all supporting test documentation shall be completed using the installed parameters as defined by the applicable protection Study and reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |  |
| Item |  | Secondary Injection Vendor Document Name/ Type | Appended to ITR (Initial) |  |  |  |

| STAGE 2 POST ENERGISATION PROTECTION INTERTRIP(S) VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | List, Confirm and Record all Metering Panel, Incomer, Feeder Receiving and Transmitting hardwired and software Intertrips. |  |  |  |

| FUNCTION AND PROTECTION INTERTRIPS & END TO END N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  |  | Serial No.: |  |  |  | Calibration Date: |  |  |  |  |
| Test Equipment: |  |  |  |  | Serial No.: |  |  |  | Calibration Date: |  |  |  |  |
| INTERTRIP 1 DESCRIPTION: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Origin |  | Destination |  | Intertrip Method |  |  |  | Pass / Fail |  | Remarks |  |  |  |
|  |  |  |  | Hard Wired |  | I/O | SOFT |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Pass Fail |  |  |  |  |  |
|  |  |  |  | Trip Relay ID: |  |  |  |  |  |  |  |  |  |
| INTERTRIP 2 DESCRIPTION: N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Origin |  | Destination |  | Intertrip Method |  |  |  | Pass / Fail |  | Remarks |  |  |  |
|  |  |  |  | Hard Wired |  | I/O | SOFT |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Pass Fail |  |  |  |  |  |
|  |  |  |  | Trip Relay ID: |  |  |  |  |  |  |  |  |  |
| INTERTRIP 3 DESCRIPTION: N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Origin |  | Destination |  | Intertrip Method |  |  |  | Pass / Fail |  | Remarks |  |  |  |
|  |  |  |  | Hard Wired |  | I/O | SOFT |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Pass Fail |  |  |  |  |  |
|  |  |  |  | Trip Relay ID: |  |  |  |  |  |  |  |  |  |
| INTERTRIP 4 DESCRIPTION: N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Origin |  | Destination |  | Intertrip Method |  |  |  | Pass / Fail |  | Remarks |  |  |  |
|  |  |  |  | Hard Wired |  | I/O | SOFT |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Pass Fail |  |  |  |  |  |
|  |  |  |  | Trip Relay ID: |  |  |  |  |  |  |  |  |  |
| Note Supporting Documentation: As a minimum all supporting test documentation shall be completed using the installed parameters as defined by the applicable protection study and reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Results are within Protection Functionality and Design Parameters Y N |  |  |  |  |  |  |  |  |  |  |
| Item | Description |  |  |  |  |  |  |  |  |  | OK | N/A | Punch |
|  | Confirm all Intertrip Safety Related Control Function (SRCF) PLC I/O - Status, Indication and Values are in accordance with functionality and design. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Confirm all SCADA - Status, Indication and Values are in accordance with functionality and design. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Confirm panel/ module trip supervision status indicators are operating as per design. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Remove all forces, bridges or links implemented to facilitate function testing. |  |  |  |  |  |  |  |  |  |  |  |  |

| STAGE 2 POST ENERGISATION TRANSFORMER PROTECTION VERIFICATION & RECORDS N/A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all Transformer Safety Related Control Function (SRCF) PLC I/O - Status, Indication and Values are in accordance with functionality and design. |  |  |  |
|  | Confirm TX Oil Low Level Trip I/O and trip function and indication (l<). |  |  |  |
|  | Confirm TX Oil Temperature Warning and/or Oil Temperature Trip I/O and trip function and indication (t>). |  |  |  |
|  | Confirm TX Pressure relief I/O and trip function and indication (p>). |  |  |  |
|  | Confirm Other TX trip function and indication:_______________________________________. |  |  |  |
|  | Confirm all SCADA - Status, Indication and Values are in accordance with functionality and design. |  |  |  |
|  | Remove all forces, bridges or links required to facilitate function testing. |  |  |  |
|  | Reset all manual indicators and manual alarm setpoints to design specifications. |  |  |  |
|  | Record the TX Tap position ___________. |  |  |  |

| PROTECTION RELAY PRIMARY INJECTION VERIFICATION & RECORDS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Primary Injection verification is only applicable to CT’s only it is not applicable to main circuit Bus systems |  |  |  |  |  |  |
| Only Required if Factory Test Results Not Available N/A |  |  |  |  |  |  |
| Item | Description |  |  | OK | N/A | Punch |
|  | If applicable, for the applicable protection elements identified carry out the required primary Injection tests. |  |  |  |  |  |
|  | List and attach the test instrument results or Vendor test documentation to this ITR. |  |  |  |  |  |
|  | Confirm all that all test results measured and expected are within manufacturers operating specifications. |  |  |  |  |  |
|  | Confirm AS-Left Parameters recorded. |  |  |  |  |  |
| Note: Primary Injection records as stipulated in the applicable System COMP shall be attached as supporting documentation. As a minimum all supporting test documentation shall be completed using the installed parameters as defined by the applicable Protection Report and reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |  |
| Test Equipment: |  | Serial No.: | Calibration Date: |  |  |  |
| Test Equipment: |  | Serial No.: | Calibration Date: |  |  |  |
| Item | Vendor Document Name / Type |  | Appended to ITR (Initial) |  |  |  |

| STAGE 2 POST ENERGISATION PROTECTION INTERTRIP VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all internal covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm all protection setting parameters and setting files have been As-commissioned and Configuration files have been collated ready for handover. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker / Qualified Engineer. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |