| Tag No. «Name» - «Description» |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |
| Drawing No. |  | «DocumentList» |  | Task No. |  | «TaskName» |
| Additional Information: |  | «Comments» |  |  |  |  |
| PANEL/MODULE CIRCUIT BREAKER/ INCOMER/ FEEDER/ EQUIPMENT DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | PDP/MCC No. |  |  |  |
| Size (A) |  |  | Panel/Tier No. |  |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS & PHYSICAL CHECKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR Task Asset and Asset Tag Identification. |  |  |  |
|  | Confirm As-Constructed Red-Line Drawings available. |  |  |  |
|  | Confirm related Function & Protection ITR E2.063 has been completed. Note: If applicable consideration should be given to protections settings for first energisation. |  |  |  |
|  | Confirm all downstream HV &LV circuits not part of this energisation are under permit of isolation, disconnected, identified and made safe (if applicable.) |  |  |  |
|  | Confirm panel arc flash rating has been identified and labelled. |  |  |  |
|  | Confirm all post energisation physical test and verification points have been identified and applicable arc flash category PPE identified and available. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and check of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all HV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | If applicable and it does not require disruption to terminations or downstream equipment, carry out the applicable pre-energisation IR check and record your results in the table below. |  |  |  |

| PRE-ENERGISATION HV INSULATION RESISTANCE (IR) TEST N/A |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  |  | Calibration Due Date: |  |  |  |
| Test Point | R to W |  | R to B | W to B |  |  | R/W/B to E |  |
| Test Voltage | 5 kVDC - 10 kVDC |  | 5 kVDC – 10 kVDC | 5 kVDC – 10 kVDC |  |  | 5 kVDC – 10 kVDC |  |
| Test Duration |  |  |  |  |  |  |  |  |
| Closed Result (MΩ) | MΩ |  | MΩ | MΩ |  |  | MΩ |  |
| Open Result (MΩ) | MΩ |  | MΩ | MΩ |  |  | MΩ |  |
| Insulation Resistance Compliance |  |  |  |  |  | Pass |  | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all internal covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm LV Aux equipment has been left in the correct state to support progressive energisation. |  |  |  |
|  | Confirm correct access and control service locks are available and installed to support energisation. |  |  |  |

| LV & ELV AUXILIARY CONTROL SUPPLY ENERGISATION PHYSICAL |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm energisation of all auxiliary control supplies. |  |  |  |

| AUXILIARY LIGHTING & HEATER SUPPLY ENERGISATION PHYSICAL VERIFICATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm energisation Panel/ Module Lighting & Heater supplies. |  |  |  |

| STAGE 2 PRE-ENERGISATION FUNCTION & PHYSICAL VERIFICATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm PLC & SCADA communication - healthy status and indication. |  |  |  |
|  | Confirm protection relay communication - healthy status and indication. |  |  |  |
|  | Confirm mechanical indication is as per physical position. |  |  |  |
|  | Confirm electrical position indication is as per physical position. |  |  |  |
|  | Confirm panel/ module status indicators are operating. |  |  |  |
|  | Confirm gas charge indicator is in the green. |  |  |  |
|  | Record gas Pressure: |  |  |  |
|  | Confirm the apparatus is in the correct position for forward switching. |  |  |  |
| Note: If applicable, consideration must be given to transformer tap positions if closing an incomer onto a parallel TX bus. |  |  |  |  |
|  | Confirm switching program is approved and switching authority has been given to proceed with switching program. |  |  |  |
|  | As per switching program, remotely operate the isolator, switch, incomer or feeder. |  |  |  |
|  | As per switching program (if applicable), locally operate or pendant operate the Isolator, switch, incomer or feeder. |  |  |  |

| STAGE 2 POST ENERGISATION VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Once energised, confirm panel/ module status indicators are as expected. |  |  |  |
|  | Once energised, confirm protection and SCADA healthy status and alarms. |  |  |  |
|  | Once energised, confirm from available test points or indication the phasing, polarity, voltage and phase rotation and record the results in the table below. |  |  |  |

| HIGH VOLTAGE PHASING, POLARITY, VOLTAGE & PHASE ROTATION |  |  |  |
| --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: | Calibration Date: |
| Test Equipment: |  | Serial No.: | Calibration Date: |
| HV Supply Voltage: 3.3 kV 6.6 kV 11 kV 33 kV Other ______________ |  |  |  |
| Indicating Instrument Type: |  |  |  |
| Test Points |  | Voltage Result | Remarks |
| 3ø R - R | N/A Phasing OK |  | Pass Fail |
| 3ø W - W | N/A Phasing OK |  | Pass Fail |
| 3ø B - B | N/A Phasing OK |  | Pass Fail |
| 3ø R - W | N/A | Voltage Indicated ________ | Pass Fail |
| 3ø R - B | N/A | Voltage Indicated ________ | Pass Fail |
| 3ø W - B | N/A | Voltage Indicated ________ | Pass Fail |
| 3ø R - N | N/A Polarity OK | Voltage Indicated ________ | Pass Fail |
| 3ø W - N | N/A Polarity OK | Voltage Indicated ________ | Pass Fail |
| 3ø B - N | N/A Polarity OK | Voltage Indicated ________ | Pass Fail |
| 3ø R - E | N/A Polarity OK |  | Pass Fail |
| 3ø W - E | N/A Polarity OK |  | Pass Fail |
| 3ø B - E | N/A Polarity OK |  | Pass Fail |
| 3ø (RWB) Phase Rotation |  | RWB Clockwise | RWB Anti-Clockwise |
| Phase Indication |  | Phase Indication Installed | Phase Indication Functioning |
|  |  | Polarity, Voltage, Phase Indication & Phase Rotation Acceptable Y N |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm the above test or indicated Voltages reflect the PLC & SCADA value. |  |  |  |
|  | Confirm apparatus stability. |  |  |  |
|  | Confirm service locks are in the correct in-service configuration and locked. |  |  |  |
|  | If applicable, confirm control selector is set to Auto/Remote. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |