| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cable Type: | «CableType» |  | Cable Rating: | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| HV INLINE JOINT INSPECTION |  |  |  |
| --- | --- | --- | --- |
| Manufacturer: |  | OEM Part Number: |  |
| Cable No: |  | From (Source) |  |
| Cable type: |  | To (Destination) |  |
| Rated Voltage: |  | Approximate Length |  |
| Conductor Type & Size |  |  |  |

| PRE-REQUISITES |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Obtain Vendor Joint Kit Manual or Installation Details. |  |  |  |
|  | Obtain Sheath Bonding and Earthing typical or General Arrangement Drawings. |  |  |  |
|  | Obtain Pit and Joint Typical or General Arrangement Drawings. |  |  |  |
|  | Confirm all test equipment is within current test date (calibration and operation). |  |  |  |
|  | Obtain Cable Drum Test results, Cable Haul/Pull Sheet Installation Records and any additional Cable laying ITR completed prior to Jointing. |  |  |  |
|  | Obtain Single Line or Cable Route diagrams and confirm location. |  |  |  |
| ITEM | PHYSICAL CHECKS | OK | N/A | Punch |
|  | Confirm positive identification of cables. |  |  |  |
|  | Confirm the cables are de-energised and earthed. |  |  |  |
|  | Confirm all test equipment is within current test date (calibration and operation). |  |  |  |
|  | Confirm all HV earth connections, surge diverters and earth grid resistance are complete. |  |  |  |
|  | Confirm cable is correct size and numbered correctly at both ends as per cable schedule. |  |  |  |
|  | Confirm Pit and Link box access is suitable and not impeded or impacted from concurrent activities. |  |  |  |
|  | Confirm cable bending radius has not been exceeded. |  |  |  |
|  | Confirm Environmental conditions are suitable for the duration of the HV Joint. |  |  |  |

| IN LINE TERMINATION KIT DETAILS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item | Type |  | Manufacturer |  |  | Serial No. |
|  | Type: |  | CAT No: |  |  | Serial No: |
|  | Type: |  | CAT No: |  |  | Serial No: |
|  | Type: |  | CAT No: |  |  | Serial No: |
| TERMINATIONS PERFORMED BY CONTRACTOR: |  |  |  |  |  |  |
| Name: |  |  |  | EW Licence No. |  |  |
| Signature: |  |  |  | Date: |  |  |

| TERMINATION ENVIRONMENTAL CONDITIONS |  |  |  |
| --- | --- | --- | --- |
| GPS Coordinates |  | Ground Conditions |  |
| Joint Depth below RL |  | Temperature |  |
| Date |  | Humidity |  |

| PHASE & CONTINUITY TEST |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: |  |  | Calibration Date: |  |
| Test Connections |  | Phase Marking & Point to Point Check |  |  | Continuity Check – Result Ω |  |
|  |  | Cable A |  | Cable B | Cable A | Cable B |
| R-R |  |  |  |  | Ω | Ω |
| B-B |  |  |  |  | Ω | Ω |
| W-W |  |  |  |  | Ω | Ω |
| A End - Cable Type: |  |  | B End – Cable Type: |  |  |  |
| A End – Cable Size: |  |  | B End – Cable Size: |  |  |  |
| Phase Point to Point Confirmed Y N |  |  | Continuity Compliance Pass Fail |  |  |  |

| PRE JOINTING CONDUCTOR INSULATION RESISTANCE (IR) TEST |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cable A – Record Cable Number: |  |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No. |  | Calibration Date: |  |  |
| Test Point | R - (W + B + R:Scn + E) | W - (R + B + W:Scn + E) |  | B - (W + R + B:Scn + E) |  | R/W/B to Screen(s)+E |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |
| Test Duration |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |
| Cable B – Record Cable Number: |  |  |  |  |  |  |  |
| Test Point | R - (W + B + R:Scn + E) | W - (R + B + W:Scn + E) |  | B - (W + R + B:Scn + E) |  | R/W/B to Screen(s)+E |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |
| Test Duration |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |

| PRE JOINTING SHEATH INTEGRITY (IR) TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cable A |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No. |  | Calibration Date: |  |  |  |
| Test Point | R:Screen to Earth | W:Screen-Earth |  | B:Screen-Earth |  | R/W/B:Screen - Earth |  |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |
| Cable B |  |  |  |  |  |  |  |  |
| Test Point | R:Screen to Earth | W:Screen-Earth |  | B:Screen-Earth |  | R/W/B:Screen - Earth |  |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| JOINT BAY CONTACT RESISTANCE TEST Only applicable to HV Joints installed with Cross Link Boxes N/A |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Date: |  |  |  |
| Joint Bay / Pit Location Identification Number: |  |  |  | Link Box Number: |  |  |  |
| Sheath+Links to SVL | Micro Ohms |  | SVL to E-Bar |  | Micro Ohms |  |  |
| R:Screen | µΩ |  | R Phase SVL |  | µΩ |  |  |
| W:Screen | µΩ |  | W Phase SVL |  | µΩ |  |  |
| B:Screen | µΩ |  | B Phase SVL |  | µΩ |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |
| Note: If Individual Joint Bay SVL testing is required attach test results |  |  |  |  |  |  |  |
| Joint Sheath Contact Resistance with links in Normal Position Compliance: |  |  |  |  |  | Pass | Fail |
| Note : Earth Stake & Grid Tests to Link Box E-Bar are to completed via the applicable Earth Stake & Grid ITR |  |  |  |  |  |  |  |

| END TO END JOINT TESTS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sheath Contact Resistance |  |  |  |  |  |  |  |
| Test Equipment |  |  | Serial No. |  | Calibration Date: |  |  |
| Phase | milli Ohms | Measured Volts | Measured Current | Calculated R (mΩ) | Length (m) (route length x 2) |  | Calculated (Ω/m) |
| R-W | mΩ |  |  |  |  |  |  |
| W-B | mΩ |  |  |  |  |  |  |
| B-R | mΩ |  |  |  |  |  |  |
|  |  |  |  | Average Cable Temperature: |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |
| Joint Sheath Contact Resistance Compliance: |  |  |  |  |  | Pass | Fail |
| Conductor Contact Resistance |  |  |  |  |  |  |  |
| Test Equipment |  |  | Serial No. |  | Calibration Date: |  |  |
| Phase | Milli Ohms | Measured Volts | Measured Current | Calculated R (mΩ) | Length (m) (route length x 2) |  | Calculated (Ω/m) |
| R-W | mΩ |  |  |  |  |  |  |
| W-B | mΩ |  |  |  |  |  |  |
| B-R | mΩ |  |  |  |  |  |  |
|  | Results Attached |  |  | Average Cable Temperature: |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |
| Joint Conductor Contact Resistance Compliance: |  |  |  |  |  | Pass | Fail |

| POST JOINTING CONDUCTOR INSULATION RESISTANCE (IR) TEST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. |  | Calibration Date: |  |  |  |  |
| Test Point | R to WBE | B to RWE |  | W to RBE |  |  |  | R/W/B to E |  |
| Test Voltage | 5 kVDC - 10 kVDC | 5 kVDC – 10 kVDC |  | 5 kVDC – 10 kVDC |  |  |  | 5 kVDC – 10 kVDC |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Result (MΩ) |  |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass |  | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all cables are discharged to Earth: |  |  |  |
|  | Confirm all cables post-test are reinstated to their normal operating positions. |  |  |  |
|  | Confirm the termination bolts used on all connection points are the correct type and size and are torqued as per the manufacturer’s recommendations. |  |  |  |
|  | Confirm Enclosure surround - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm all cables entering the link box are sealed at the lug to prevent the ingress of moisture within the link cable. |  |  |  |
|  | Confirm all cables are marked and labels/nameplates fitted to Cable Pit and Link Box. |  |  |  |
|  | Confirm all link box and Pit lids are reinstated are water tight and tightened to the correct torque. |  |  |  |
| Note: Offline Partial Discharge and/or Tan-Delta Testing of the jointed cable will be required prior to final Termination |  |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Digital photos required: In-line joints and cable terminations prior to replacing covers. Digital photos of significant terminations are to be identified and submitted with this ITR. |  |  |  |
| Photo ID |  | Description | Taken By |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |