| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. |  |  |  |
|  | Confirm Layout, location and orientation is correct against design drawings. |  |  |  |
|  | Confirm equipment is level, details of foundation / plinth and clearance distances are as per design. |  |  |  |
|  | Confirm Manufactures applicable Type and Routine Tests as per the data sheet and applicable standards have been completed and evidence provided. Manufacturers testing must include applicable Power Frequency withstand and impulse tests for main circuits and auxiliary circuits. |  |  |  |
|  | Confirm front and rear signage is as per design. |  |  |  |
|  | Confirm ARC Flash Hazard labels are fitted. |  |  |  |
|  | Confirm equipment is free from damage and debris. |  |  |  |
|  | Confirm door seals are secure and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm cable enclosures are sealed and secured. |  |  |  |
|  | Confirm glands are properly installed as per manufacturer’s recommendations and unused cable entries plugged. |  |  |  |
|  | Confirm control wiring is consistent with schematic drawings. |  |  |  |
|  | Confirm Segregation and separation of ELV and LV blocks and terminals. |  |  |  |
|  | Confirm Ducting covers are fitted and wiring looms are neat and tidy. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm Isolators, Bus Tie and Earth switches for correct installation, alignment, mechanical operation and correct mechanical interlock functionality. |  |  |  |
|  | Confirm Fortress key identification and scheme functionality. |  |  |  |
|  | Confirm the gas pressure (if applicable). |  |  |  |
|  | Confirm all position indications are correct. |  |  |  |
|  | Confirm that all main circuit terminations are tight and where torque settings are required, that correct values have been obtained and connection has been marked to indicate completion. |  |  |  |
|  | Confirm inspection of bus expansion joints post transport. |  |  |  |
|  | Confirm phase markers/ indication has been fitted where required. |  |  |  |
|  | Confirm panel enclosure live line indication elements are positioned, installed and terminated correctly. |  |  |  |
|  | Confirm panel enclosure space heaters are positioned, installed and terminated correctly. |  |  |  |
|  | Confirm panel enclosure interior lighting is positioned, installed and terminated as per the GA and termination drawings. |  |  |  |
|  | Confirm gland plates are earthed, sealed and secured. |  |  |  |
|  | Confirm Earth Bars and Main Earth Cables type, size and installation is as per design. |  |  |  |
|  | Confirm panel and door earthing is correct and as per design. |  |  |  |
|  | Confirm ARC vents are clear and unobstructed. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| CONTINUITY, PHASING & EARTH |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R |  | Ω |
| W-W |  | Ω |
| B-B |  | Ω |
| Main E- E Bar |  | Ω |
| Point to Point Confirmed Y N | Continuity OK Pass Fail | Phase Markings Confirmed Y N |

| BUS ASSEMBLY INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Incomer, Feeder, CB, ISOL, Earth Switch, Bus Ties - OPEN |  |  |  |  |  |  |  |  |  |
| Test Equipment |  | Serial No. |  |  | Calibration Due Date: |  |  |  |  |
| Test Point | R to W |  | R to B | W to B |  |  | R/W/B to E |  |  |
| Test Voltage | 5 kVDC |  | 5 kVDC | 5 kVDC |  |  | 5 kVDC |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Result (GΩ) | GΩ |  | GΩ | GΩ |  |  | GΩ |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass | Fail |

| HIGH VOLTAGE DIELECTRIC WITHSTAND LEAKAGE TEST (HiPot) N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test to be conducted @75% Routine - Only if manufacturers Routine Test data is not available |  |  |  |  |  |  |  |  |  |
| HV withstand only required on switchgear 11kV and above - Incomer, Feeder, CB, ISOL, Earth Switch, Bus Ties - OPEN |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. |  | Calibration Date: |  |  |  |
| Duration: _______ | Test Voltage/ Freq. | IR (MΩ) | @ 100% |  | @ 75% |  | @ 90% |  |  |
| Test Configuration |  |  | Leakage Current (mA) |  | Leakage Current (mA) |  | Leakage Current (mA) |  |  |
| R - (W + B + E) | / |  |  |  |  |  |  |  |  |
| W - (R + B + E) | / |  |  |  |  |  |  |  |  |
| B - (W + R + E) | / |  |  |  |  |  |  |  |  |
| (R + W + B) – (E) | / |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass | Fail |

| POST HV DIELECTRIC WITHSTAND BUS ASSEMBLY INSULATION RESISTANCE TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |
| Test Point | (R+W+B)-E |  |  |  |  |  |
| Test Voltage | 5 kVDC |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |
| Result (GΩ) | GΩ |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  | Pass | Fail |

| CONTACT RESISTANCE - DUCTOR TEST |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |  |  |
| Note: Phase Ref Point from Panel 1 |  |  | Note: |  |  |  |  |  |  |  |  |
| At point of supply | Micro Ohms | At point of supply |  | Micro Ohms | At point of supply | Micro Ohms |  | At point of supply |  | Micro Ohms |  |
|  | Ref R |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | Ref W |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | Ref B |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | Ref N |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | Ref E |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
|  | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
| Note: Attach General Arrangement Drawing indicating Panel Identification and test point location to support results. |  |  |  |  |  |  |  |  |  |  |  |
| Contact Resistance Test Current: Contact Resistance Test Compliance |  |  |  |  |  |  |  |  | Pass |  | Fail |

| POST-TESTING VERIFICATIONS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all bus sections are discharged to Earth. |  |  |  |
|  | Confirm Torque Checks completed. |  |  |  |
|  | Confirm enclosure integrity and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm HV MCC/ LC is left clean, free from debris and test tools. |  |  |  |
|  | Replace all covers and confirm the HV MCC/ HV LC is safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |