| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cable Type: | «CableType» |  | Cable Rating: | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm cable route and to and from equipment locations are correct as per the cable schedule/ routing layout. |  |  |  |
|  | Confirm the cable size and type is correct, and cable is labelled at both ends as per the cable schedule. |  |  |  |
|  | Confirm cable support and enclosure systems are installed correctly and secure. |  |  |  |
|  | Confirm cable bending radius has not been exceeded. |  |  |  |
|  | Confirm cable installation completed as per project specs and with no visible signs of stress. |  |  |  |
|  | Confirm cable glands are of correct type, correct size and have been installed and tightened to the correct specification. |  |  |  |
|  | If applicable, confirm cable armouring and screen earthed as per design. |  |  |  |
|  | Confirm cable lugs are correct type & size with adequate surface contact area. |  |  |  |
|  | Confirm lugs have the correct hole size and holes have not been modified or altered. |  |  |  |

| TERMINATION KIT DETAILS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item | Termination Point |  | Termination Kit Type |  | Termination Kit Serial No. |  |
|  | R - Source |  | CAT No: |  | Serial No: |  |
|  | R - Destination |  | CAT No: |  | Serial No: |  |
|  | W - Source |  | CAT No: |  | Serial No: |  |
|  | W - Destination |  | CAT No: |  | Serial No: |  |
|  | B - Source |  | CAT No: |  | Serial No: |  |
|  | B - Destination |  | CAT No: |  | Serial No: |  |
| TERMINATIONS PERFORMED BY CONTRACTOR: |  |  |  |  |  |  |
| Name: |  |  |  | EW Licence No. |  |  |
| Signature: |  |  |  | Date: |  |  |

| PHASING & CONTINUITY TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Connections | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R:Scn | R-R | Ω |
| W-W:Scn | W-W | Ω |
| B-B:Scn | B-B | Ω |
|  | Phase Point to Point Confirmed Y N | Continuity Compliance Pass Fail |

| CONDUCTOR INSULATION RESISTANCE (IR) TEST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  | Calibration Date: |  |  |  |  |
| Test Point | R - (W + B + R:Scn + E) | W - (R + B + W:Scn + E) |  | B - (W + R + B:Scn + E) |  | R/W/B to Screen(s)+E |  |  |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |  |

| SHEATH INTEGRITY (IR) TEST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  | Calibration Date: |  |  |  |  |
| Test Point | R:Screen to Earth | W:Screen-Earth |  | B:Screen-Earth |  | R/W/B:Screen - Earth |  |  |  |
| Test Voltage | 1 kVDC | 1 kVDC |  | 1 kVDC |  | 1 kVDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |  |

| HIGH VOLTAGE WITHSTAND TEST - (VLF) NEW CABLES ONLY N/A |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. |  | Calibration Date |  |  |  |
| Duration: 60min | Test Voltage | Peak Voltage |  | VLF @ 0.1 Hz – 1 Min | VLF @ 0.1 Hz – 15 Min |  | VLF @ 0.1 Hz – 60 Min |  |
| Test Configuration |  |  |  | Start Leakage Current (mA) | Leakage Current (mA) |  | Finish Leakage Current (mA) |  |
| R - (W + B + R:Scn + E) |  |  |  |  |  |  |  |  |
| W - (R + B + W:Scn + E) |  |  |  |  |  |  |  |  |
| B - (W + R + B:Scn + E) |  |  |  |  |  |  |  |  |
| (R + W + B) – (R/W/B:Scn + E) |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass |  | Fail |

| OFFLINE PARTIAL DISCHARGE AND TAN-DELTA DIAGNOSTIC TEST |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Note: Partial Discharge & Tan-Delta tests are only valid for cable with synthetic insulation, and is not valid for test on self-healing insulating media, like air or vacuum. |  |  |  |  |  |  |  |  |  |  |  |
| Partial Discharge Test Equipment |  |  |  | Serial No. |  |  |  |  | Calibration Date: |  |  |
| Tan-Delta Test Equipment |  |  |  | Serial No. |  |  |  |  | Calibration Date: |  |  |
| Partial Discharge Test Required |  |  |  |  |  | Tan-Delta Test Required |  |  |  |  |  |
| Test Point | Red Phase (pC) |  | Red Phase (DDF) |  | White Phase (pC) |  |  | White Phase (DDF) |  | Blue Phase (pC) | Blue Phase (DDF) |
| Test Voltage |  |  |  |  |  |  |  |  |  |  |  |
| 0.3 Uo |  |  |  |  |  |  |  |  |  |  |  |
| 0.6 Uo |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 Uo |  |  |  |  |  |  |  |  |  |  |  |
| 1.0 Uo |  |  |  |  |  |  |  |  |  |  |  |
| 1.3 Uo |  |  |  |  |  |  |  |  |  |  |  |
| 1.5 Uo |  |  |  |  |  |  |  |  |  |  |  |
| 1.7 Uo |  |  |  |  |  |  |  |  |  |  |  |
| **2.0 Uo |  |  |  |  |  |  |  |  |  |  |  |
| Note: Uo = VN / √3 |  |  |  |  |  |  |  |  |  |  |  |
| Note: Test Equipment Results – Minimum Requirements: **Note Existing Cables not to be tested above 1.7 Uo PD test should be terminated if PD activity >5000pC is detected. • Background noise • PD Inception Voltage • PD @ 1.0 Uo • PD @ 1.7 Uo • PD @ Extinction Voltage • Location & Severity. Please attach all printouts of software-generated PD patterns and results. |  |  |  |  |  |  | Note: Test Equipment Results – Minimum Requirements: **Note Existing Cables not to be tested above 1.7 Uo TD Test should be terminated if a poor Tip-up value is detected Pre-test expectations and Results are determined as per IEEE Std 400.2 Please attach all printouts of software-generated Tan Delta patterns and results. |  |  |  |  |
| PD Test Complete (Engineer) Pass Fail |  |  |  |  |  |  | TAN-DELTA Test Complete (Engineer) Pass Fail |  |  |  |  |

| POST VLF- CONDUCTOR INSULATION RESISTANCE (IR) TEST N/A |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  | Calibration Date: |  |  |
| Test Point | R - (W + B + R:Scn + E) | W - (R + B + W:Scn + E) |  | B - (W + R + B:Scn + E)W to RBE |  | R/W/B to Screen(s)+E |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |
| Test Duration |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all cables are discharged to Earth. |  |  |  |
|  | Confirm the termination bolts used on all connection points are the correct type and size and are torqued as per the manufacturers recommendations. Record torque settings in the table below. |  |  |  |

| CONTACT RESISTANCE (DUCTOR) TEST |  |  |  |  |  |  | BOLT TORQUE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  |  | Serial No: |  |  |  |  | Calibration. Date: |  |  |
| Torque Wrench: |  |  |  |  | Serial No: |  |  |  |  | Calibration. Date: |  |  |
| At Source |  | Micro Ohms | At Destination | Micro Ohms |  |  | At point of supply |  | Torque Nm |  | At point of destination | Torque Nm |
| R-R |  | µΩ | R-R | µΩ |  |  | R |  | Nm |  | R | Nm |
| W-W |  | µΩ | W-W | µΩ |  |  | W |  | Nm |  | W | Nm |
| B-B |  | µΩ | B-B | µΩ |  |  | B |  | Nm |  | B | Nm |
| R:Scn-E |  | µΩ | E-E | µΩ |  |  | R:Scn-E |  | Nm |  | R:Scn-E | Nm |
| W:Scn-E |  | µΩ | E-E | µΩ |  |  | W:Scn-E |  | Nm |  | W:Scn-E | Nm |
| B:Scn-E |  | µΩ | E-E | µΩ |  |  | B:Scn-E |  | Nm |  | B:Scn-E | Nm |
| R/W/BScn-E |  | µΩ | R/W/BScn-E | µΩ |  |  | R/W/BScn-E |  | Nm |  | R/W/BScn-E | Nm |
| Refer to SS-E115 for Test Pass Fail Criteria |  |  |  |  |  |  |  |  |  |  | Pass | Fail |
| Note: Bolt Torque is a hold point. Bolt torqueing must be witnessed by an EPCM representative prior to closing the Panel or terminal box. |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable Termination At Source (Point of Supply) EPCM Witnessed by: |  |  |  |  |  |  |  |  |  |  |  |  |
| Name: |  |  |  |  |  | Title: |  |  |  |  |  |  |
| Signature: |  |  |  |  |  | Date: |  |  |  |  |  |  |
| Cable Termination At Destination EPCM Witnessed by: |  |  |  |  |  |  |  |  |  |  |  |  |
| Name: |  |  |  |  |  | Title: |  |  |  |  |  |  |
| Signature: |  |  |  |  |  | Date: |  |  |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Enclosure integrity and terminal separation - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Digital photos required: Cable terminations prior to replacing covers. Digital photos of are to be identified below and submitted with this ITR. |  |  |  |
| Photo ID |  | Description | Taken By |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm terminal box covers are replaced. |  |  |  |
|  | Confirm Circuit Left Safe and Ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |