| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  | Model No. | «OEMPartlNumber» |
| Drawing No. | «DocumentList» |  |  | Task No. | «TaskName» |
| Additional Information: |  |  | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details as per datasheet and equipment labeling as per GA and Schematic. |  |  |  |
|  | Confirm mounting is correct, IP rating not compromised and not subject to vibration. |  |  |  |
|  | Confirm equipment is free from damage, rust, contamination and debris internally and externally. |  |  |  |
|  | Confirm location and orientation is correct. |  |  |  |
|  | Confirm glands are correctly installed and tight as per the manufacturer’s recommendations. |  |  |  |
|  | Confirm control wiring is as per design drawings. |  |  |  |
|  | Confirm all wires are ferruled and ferrules are correct. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm all Earth bonding is as per design and specifications. |  |  |  |
|  | Complete the table below for Phasing, Element Continuity and Insulation Resistance. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| CONTINUITY, PHASING & EARTH CONTINUITY |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R |  | Ω |
| W-W | N/A | Ω |
| B-B | N/A | Ω |
| N-N |  | Ω |
| E-E |  | Ω |
| E-Gland Plate |  | Ω |
| E-EP Bond |  | Ω |
| Element Resistance |  | Ω |
|  | Point to Point Confirmed Y N | Continuity Compliance Pass Fail |

| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  |  | Calibration Due Date: |  |  |  |  |
| Test Point | R to E | W to E | B to E | RWB to E |  | A to E |  |  |  |
| Test Voltage | 500VDC | 500VDC | 500VDC | 500VDC |  | 500VDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm equipment integrity, Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm equipment is left clean, free from debris and test tools. |  |  |  |
|  | Replace all covers and confirm the equipment is safe and ready for function testing. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |