| Tag No. «Name» - «Description» |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |
| Drawing No. |  | «DocumentList» |  | Task No. |  | «TaskName» |
| Additional Information: |  | «Comments» |  |  |  |  |
| PANEL/ MODULE PROTECTION RELAY DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | LC/MCC No. |  |  |  |
| Type/Model |  |  | Panel/Tier No. |  |  |  |
| PANEL/ MODULE CIRCUIT BREAKER/ INCOMER/ FEEDER / EQUIPMENT DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | Size (A) |  |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS & PHYSICAL CHECKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset and asset tag identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm Manufactures applicable Function, Protection and Routine Tests as per the data sheet, manufacturers ITP and applicable standards have been completed and evidence provided. |  |  |  |
|  | Confirm all downstream LV final sub-circuit or auxiliary circuits not part of this energisation are under isolation permit, disconnected, identified and made safe (if applicable). |  |  |  |
|  | Confirm all downstream ELV auxiliary circuits not part of this energisation are disconnected, identified and made safe (if applicable). |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and check of all earthing requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all ELV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Confirm all internal covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |

| LV & ELV AUXILIARY CONTROL SUPPLY ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Energise or confirm energisation of auxiliary control supplies. |  |  |  |
|  | Complete the panel/ module auxiliary control voltage table below for the Aux control supply. |  |  |  |

| AUX 1 - LV & ELV CONTROL AUXILLIARY SUPPLY – POLARITY & VOLTAGE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| Supply Voltage: 12 VDC 24 VDC 48 VDC 110 VDC 110 VAC 240 VAC Other ___________ |  |  |  |  |  |
| Test Location: |  |  |  |  |  |
| Test Points |  | Voltage Result |  |  | Remarks |
| A - N | N/A Polarity OK | Measured _______ Indicated ________ |  |  | Pass Fail |
| A - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
|  |  | Polarity & Voltage Acceptable Y N |  |  |  |

| STAGE 2 POST AUXILIARY ENERGISATION FUNCTION & PHYSICAL VERIFICATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm PLC & SCADA Communication - Healthy status and indication. |  |  |  |
|  | Confirm Protection Relay Communication - Healthy status and indication. |  |  |  |
|  | If applicable, manually operate the Isolator, Feeder Circuit Breaker to confirm Operation. |  |  |  |
|  | If applicable, confirm manual racking and spring charge mechanisms operate as per design. |  |  |  |
|  | If applicable, confirm mechanical interlocking and position indication is operating as per design. |  |  |  |
|  | If applicable confirm electrical interlocking and position indication is operating as per design. |  |  |  |
|  | Confirm panel/ module status indicators are operating as per design. |  |  |  |
|  | If applicable, confirm local/manual racking and spring motor charge mechanisms operate as per design. |  |  |  |
|  | If applicable, remotely operate the Isolator, Feeder to confirm Operation is as per design. |  |  |  |
|  | Confirm all Safety Related Control Function (SRCF) PLC I/O - Status, Indication and Values are in accordance with functionality and design. |  |  |  |
|  | Confirm all SCADA - Status, Indication and Values are in accordance with functionality and design. |  |  |  |

| STAGE 2 SECONDARY INJECTION PROTECTION VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Only Required if Factory Test Results Not Available N/A |  |  |  |  |
| Item | Description | OK | N/A | Punch |
|  | Record the Protection Study document number for the equipment protection parameters, discrimination, grading and relay settings. Protection Study Document Number:_____________________ |  |  |  |
|  | Confirm availability of Protection Relay Data Sheet & Manufacturers IOM Manual. |  |  |  |
|  | Confirm availability of Protection Relay /Tier Module As-built Schematics. |  |  |  |
|  | From the table below select the protection relay ANSI/IECC function codes as referenced in the Protection Study, Data sheet and from the single line and protection diagrams. |  |  |  |

| INCOMER/ FEEDER/ SWITCH/ CIRCUIT BREAKER |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Only Required if Factory Test Results Not Available N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| Earth & Neutral |  |  |  |  | Voltage & Current |  |  |  | Phase & Frequency |  |  |  |
| ANSI | Symbol | Description |  | ANSI |  | Symbol | Description |  | ANSI | Symbol | Description |  |
| 50 (N or G) | I0>> | Definitive Time Earth Fault Over Current |  | 50 |  | I>> | Instantaneous Overcurrent |  | 25 | SYNC | Synch or Synch Check Relay |  |
| 51 (N or G) | I0> | Inverse Time Earth Fault Over Current |  | 51 |  | I> | Inverse Time Over Current |  | 81 | f | Over / Under Frequency Relay |  |
|  | IΔn | Earth Leakage |  | 27 |  | U< | Under Voltage Relay |  | 79 | 0→1 | Auto Reclose |  |
| 59N | U0> | Neutral Point Displacement Relay |  | 59 |  | U> | Over Voltage Relay |  | Thermal |  |  |  |
|  |  |  |  | 68 |  | I2> | Inrush Current |  | 49F | Ith> | Thermal Prot Cables |  |
|  |  |  |  | 87 |  | ΔI> | Differential Protection |  | 49 (Tor G) |  | Thermal Prot Tx or Generator |  |
| Motor External |  |  |  | Motor Internal |  |  |  |  | Other (Record) |  |  |  |
| ANSI | Symbol | Description |  | ANSI |  | Symbol | Description |  | ANSI | Symbol | Description |  |
| 38 |  | Bearing Temperature |  | 46 |  |  | Current Unbalance |  | AFD |  | Arc Flash Detector |  |
| 49P |  | PTC Overtemp |  | 47 |  |  | Phase Reversal |  |  |  |  |  |
| 49R |  | RTD Thermal |  | 49T |  |  | Thermal Model |  |  |  |  |  |
|  |  |  |  | 66 |  |  | Starts Per Hour |  |  |  |  |  |
|  |  |  |  | 55 |  |  | Power Factor |  |  |  |  |  |
|  |  |  |  | 49M |  |  | Thermal Protection |  |  |  |  |  |

| STAGE 2 FUNCTION & PROTECTION VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm setting/ upload of Protection Relay Function Parameters and trip settings as per the Protection Study. The Manufacturers ITP will stipulate how many points shall be tested for each IDMT element. Pickup and drop off test shall be performed for each definite time element |  |  |  |

| BASIC LV PROTECTION FEEDER SETTINGS & TRIP CHARACTERISTICS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Only Required if Factory Test Results Not Available N/A |  |  |  |  |  |
| Thermal & Curve |  | Instantaneous Residual Current |  | Ground Fault Trip |  |
| CB Thermal Setting |  | Residual Current [In] |  | Pick-up Current [Ig] |  |
| CB Curve Setting |  |  |  | Time-delay [tg] |  |
| Long Time Delay |  | Short Time Delay |  | Instantaneous Trip |  |
| Pick-up Current [Ir] |  | Pick-up Current [Isd] |  | Pick-up Current [Ii] |  |
| Time-delay [tr] |  | Time-delay [tsd] |  |  |  |

| STAGE 2 FUNCTION & PROTECTION VERIFICATION & RECORDS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description |  | OK | N/A | Punch |
|  | If applicable, for all protection elements identified carry out the required secondary Injection tests. |  |  |  |  |
|  | List and attach the test instrument results or Manufacturers FAT test documentation to this ITR. |  |  |  |  |
|  | Confirm that all test results measured and expected are within manufacturers operating specifications. |  |  |  |  |
|  | Where fitted confirm Protection Supervision Relay ARC SENSOR instrument Inputs are operating as per design. |  |  |  |  |
| Secondary Injection records as stipulated in the applicable ITP or FAT system commissioning procedure shall be attached as supporting documentation. Note Supporting Documentation: As a minimum all supporting test documentation shall be completed using the installed parameters as defined by the applicable protection Study and reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |
| Item | Secondary Injection Vendor Document Name / Type | Appended to ITR (Initial) |  |  |  |

| STAGE 2 POST ENERGISATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Description |  |  |  |  | OK | N/A | Punch |
|  | Confirm all internal covers are reinstated and secure. |  |  |  |  |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |  |  |  |  |
|  | Confirm all protection setting parameters and setting files have been As-commissioned and Configuration files have been collated ready for handover. |  |  |  |  |  |  |  |
| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |  |  |
| Item |  | Description | Initial | N/A | Comments |  |  |  |
|  |  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |
|  |  | This form must be completed by an Authorised Electrical Worker. |  |  |  |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |