| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. |  |  |  |
|  | Confirm Manufactures applicable Type and Routine Tests as per the data sheet and applicable standards have been completed and evidence provided. Manufacturers testing must include applicable Power Frequency withstand tests for main circuits and auxiliary circuits. |  |  |  |
|  | Confirm equipment has no mechanical/ transport damage. |  |  |  |
|  | Confirm door seals are secure and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm Protection Relay location, installation and orientation are correct as per the design drawings. |  |  |  |
|  | Confirm Protection Relay terminal blocks and test blocks are correctly identified. |  |  |  |
|  | Confirm proper terminal block arrangement and labelling: a. Shorting and isolating for CT Circuits. b. Isolating for VT circuits. c. Solid type for Control circuits. d. Test blocks (If Fitted) |  |  |  |
|  | Confirm Segregation and separation of panel ELV and LV blocks, links and terminals. |  |  |  |
|  | If applicable, confirm fit and alignment of Test Plug. |  |  |  |
|  | Confirm control wiring is consistent with schematic drawings. |  |  |  |
|  | Confirm Ducting covers are fitted. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm circuit breaker / Isolator for correct installation, alignment mechanical manual operation and damage. |  |  |  |
|  | If applicable, confirm Fortress key identification and scheme functionality. |  |  |  |
|  | If applicable, confirm the spring charge mechanism (Manual Charge). |  |  |  |
|  | If applicable, confirm the trip operation (Mechanical). |  |  |  |
|  | If applicable, confirm the close operation (Mechanical). |  |  |  |
|  | If applicable, confirm the interlocks (Mechanical). |  |  |  |
|  | Confirm all position indications are correct. |  |  |  |
|  | Record the operations counter. ______ |  |  |  |
|  | Confirm CB enclosure live line elements are positioned, installed and terminated correctly. |  |  |  |
|  | If applicable, confirm CB enclosure Heaters pads are positioned, installed and terminated correctly. |  |  |  |
|  | If applicable, confirm CB enclosure interior lighting is positioned, installed and terminated correctly. |  |  |  |
|  | Confirm Earth Bars and Main Earth Cables type, size and installation is as per design. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| CONTINUITY, PHASING & EARTH |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| R-R |  | Ω |
| W-W |  | Ω |
| B-B |  | Ω |
| Module E-E Bar |  | Ω |
| Point to Point Confirmed Y N | Continuity Compliance Pass Fail | Phase Markers Confirmed Y N |

| ASSEMBLY INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  |  | Calibration Due Date: |  |  |  |  |  |  |
| Test Point | R to W | R to B |  | W to B |  | R to N |  |  | W to N |  | B to N |  |  |
| Test Voltage | 1 kVDC | 1 kVDC |  | 1 kVDC |  | 1 kVDC |  |  | 1 kVDC |  | 1 kVDC |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |  | MΩ |  | MΩ |  |  |
| Test Point | R to E | W to E |  | B to E |  | N to E |  |  |  |  |  |  |  |
| Test Voltage | 1 kVDC | 1 kVDC |  | 1 kVDC |  | 1 kVDC |  |  |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  |  | Pass |  | Fail |  |

| HIGH VOLTAGE DIELECTRIC WITHSTAND LEAKAGE TEST (HiPot) N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test to be conducted @75% Routine (DC) Only if manufacturers Routine Test data is not available |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No. |  |  | Calibration Date: |  |  |  |
| Duration: ______ | Test Voltage | IR (MΩ) |  | @ 100% | @ 75% |  | @ 90% |  |  |
| Test Configuration |  |  |  | Leakage Current (mA) | Leakage Current (mA) |  | Leakage Current (mA) |  |  |
| R - (W + B + E) | 2kVDC |  |  |  |  |  |  |  |  |
| W - (R + B + E) | 2kVDC |  |  |  |  |  |  |  |  |
| B - (W + R + E) | 2kVDC |  |  |  |  |  |  |  |  |
| (R + W + B) – (E) | 2kVDC |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass | Fail |

| POST HV DIELECTRIC WITHSTAND BUS ASSEMBLY INSULATION RESISTANCE TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |
| Test Point | (R+W+B)-E |  |  |  |  |  |
| Test Voltage | 1 kVDC |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  | Pass | Fail |

| CONTACT RESISTANCE - DUCTOR TEST |  |  |  |  |  | BOLT TORQUE |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  |  | Calibration. Date: |  |  |
| Torque Wrench Type: |  |  | Serial No: |  |  |  |  | Calibration. Date |  |  |
| At point of supply | Micro Ohms | At point of destination |  | Micro Ohms | Test Point |  | Torque Nm |  | Test Point | Torque Nm |
| R-R | µΩ | R-R |  | µΩ | R |  | Nm |  | R | Nm |
| W-W | µΩ | W-W |  | µΩ | W |  | Nm |  | W | Nm |
| B-B | µΩ | B-B |  | µΩ | B |  | Nm |  | B | Nm |
| E-E | µΩ | E-E |  | µΩ | R |  | Nm |  | R | Nm |
|  |  |  |  |  | W |  | Nm |  | W | Nm |
|  |  |  |  |  | B |  | Nm |  | B | Nm |
| Contact Resistance Test Current: Contact Resistance Test Compliance |  |  |  |  |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all components are discharged to Earth. |  |  |  |
|  | Confirm enclosure integrity and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm Module is left clean, free from debris and test tools. |  |  |  |
|  | Replace all covers and confirm the CB is safe and ready for function testing. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |