| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cable Type: | «CableType» |  | Cable Rating: | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm that the cable is of correct size, type and colour as stipulated in the cable schedule. |  |  |  |
|  | Confirm cable identification markings are in place. |  |  |  |
|  | Check cable and confirm there is no mechanical damage. |  |  |  |
|  | Confirm cable joint ends and destinations have been positively identified. |  |  |  |
|  | Confirm the manufacturer’s joint kit installation manual or inline joint procedures are available. |  |  |  |
|  | Confirm environmental considerations are addressed prior to joint commencement. |  |  |  |
|  | Inspect the inline termination kit for use by date, condition and all components are assembled and available prior to joint commencement. |  |  |  |
|  | Inspect and check cable terminations to ensure all splice links are crimped correctly, screw joints are secure, tight and core segregation is maintained. |  |  |  |
|  | Inspect and check cable terminations to ensure all joints are clean and free of dust prior to final sealing and waterproofing. |  |  |  |
|  | Take photos at each step of the cable joint to record progress. |  |  |  |

| IN LINE TERMINATION KIT DETAILS |  |  |  |
| --- | --- | --- | --- |
| Item | Type: | Manufacturer: | Joint Type: |
|  | Type: | CAT No: | Serial No: |
|  | Type: | CAT No: | Serial No: |
|  | Type: | CAT No: | Serial No: |

| PHASE & CONTINUITY TEST |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: |  |  | Calibration Date: |  |  |
| Test Connections |  | Phase Marking Check |  |  | Continuity Check – Result Ω |  |  |
|  |  | Cable A |  | Cable B | Cable A | Cable B |  |
| R-R |  |  |  |  | Ω |  | Ω |
| B-B |  |  |  |  | Ω |  | Ω |
| W-W |  |  |  |  | Ω |  | Ω |
| N-N |  |  |  |  | Ω |  | Ω |
| E-E |  |  |  |  | Ω |  | Ω |
| Source (A) - Cable Type: |  |  | Destination (B) – Cable Type: |  |  |  |  |
| Source (A) - Cable Size: |  |  | Destination (B) – Cable Size: |  |  |  |  |
| Phasing Point to Point Confirmed Y N |  | Continuity Compliance Pass Fail |  |  |  |  |  |

| JOINT INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. |  |  | Calibration Date: |  |  |
| Test Point | R to W | R to B | W to B | R to N | W to N | B to N | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Photo ID |  | Description | Taken By |

| IN LINE SPLICE JOINT CONTACT RESISTANCE (DUCTOR) TEST (For cables ≥70 mm2) Not Achievable N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: | Serial No: |  | Calibration. Date: |  |  |
| At point of supply | Micro Ohms | At point of destination |  | Micro Ohms |  |
| R-R | µΩ | R-R |  | µΩ |  |
| W-W | µΩ | W-W |  | µΩ |  |
| B-B | µΩ | B-B |  | µΩ |  |
| N-N | µΩ | N-N |  | µΩ |  |
| E-E | µΩ | E-E |  | µΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all cables are discharged to Earth. |  |  |  |
|  | Confirm that cable identification is attached near the joint so the cable joint is identified. |  |  |  |
|  | If possible, record the joint GPS location on a general arrangement drawing and attach to this ITR. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |