| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Cable Type: | «CableType» |  |  | Cable Rating: | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |  |
| From: | «CableFrom» | To: | «CableTo» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |  |
| Additional Information: | «Comments» |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm that the cable is of correct size, type and colour as stipulated in the cable schedule. |  |  |  |
|  | Confirm cable identification markings are in place. |  |  |  |
|  | Check cable and confirm there is no mechanical damage. |  |  |  |
|  | Confirm cable route and to and from equipment locations are correct as per the cable schedule/ routing layout. |  |  |  |
|  | Confirm cable cores are numbered correctly at both ends as per cable schedule. |  |  |  |
|  | Confirm that ferrule numbers are in place where required and are correct. |  |  |  |
|  | Confirm segregation between the cables with different voltage levels is maintained as per the design. |  |  |  |
|  | Confirm all terminations are tight and where torque settings are required, that correct values have been obtained and the connection has been marked to indicate completion. |  |  |  |
|  | Confirm that earth cable has been terminated in accordance with schematic. |  |  |  |
|  | Confirm cable support and enclosure systems are satisfactory and secure. |  |  |  |
|  | Confirm that the minimum cable bending radius has not been exceeded. |  |  |  |
|  | Confirm cable installed as per the cable layout drawings and project specs. |  |  |  |
|  | Confirm correct cable glands for cable type, glands are screwed as per manufacturer’s instructions. |  |  |  |
|  | Confirm cable termination to ensure all lugs/pins are crimped correctly, nuts, washers and spring washers are in place and terminals are clean and free of dust. |  |  |  |
|  | Confirm cable armouring earthed as per design. |  |  |  |
|  | Confirm that all spare cores are terminated and are earthed at one end. |  |  |  |
|  | Confirm phase markings (RWB) and continuity of active conductors is correct. |  |  |  |
|  | Digital photos required for drives 90 kW and above, or cable 70 mm2 and above. |  |  |  |

| PHASING & CONTINUITY TEST |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No.: |  |  |  | Calibration Date: |  |  |  |
| Test Connections |  |  |  | Point to Point Check (Initial Pass/Fail) |  |  |  | Continuity Check – Result Ω |  |  |  |
| R |  |  |  | R-R |  |  |  | Ω |  |  |  |
| W |  |  |  | W-W |  |  |  | Ω |  |  |  |
| B |  |  |  | B-B |  |  |  | Ω |  |  |  |
| N |  |  |  | N-N |  |  |  | Ω |  |  |  |
| E |  |  |  | E-E |  |  |  | Ω |  |  |  |
|  |  |  |  | Phase Point to Point Confirmed Y N |  |  |  | Continuity Confirmed Pass Fail |  |  |  |
| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment |  |  |  | Serial No. |  |  |  | Calibration Date: |  |  |  |
| Test Point | R to W | R to B |  | W to B | R to N | W to N |  | B to N | RWB to E | N to E |  |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC | 500 VDC | 500 VDC |  | 500 VDC | 500 VDC | 500 VDC |  |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ | MΩ | MΩ |  | MΩ | MΩ | MΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  | Pass | Fail |  |

| CONTACT RESISTANCE (DUCTOR) TEST (For cables ≥70 mm2) |  |  |  |  | BOLT TORQUE (For cables ≥70 mm2) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No: |  |  |  |  | Calibration. Date: |  |  |
| Torque Wrench: |  |  | Serial No: |  |  |  |  | Calibration. Date: |  |  |
| At point of supply | Micro Ohms | At point of destination |  | Micro Ohms |  | At point of supply | Torque Nm |  | At point of destination | Torque Nm |
| R-R | µΩ | R-R |  | µΩ |  | R | Nm |  | R | Nm |
| W-W | µΩ | W-W |  | µΩ |  | W | Nm |  | W | Nm |
| B-B | µΩ | B-B |  | µΩ |  | B | Nm |  | B | Nm |
| N-N | µΩ | N-N |  | µΩ |  | N | Nm |  | N | Nm |
| E-E | µΩ | E-E |  | µΩ |  | E | Nm |  | E | Nm |

| Refer to SS-E115 for Test Pass Fail Criteria | Pass | Fail |
| --- | --- | --- |

| Note: For cables ≥70 mm2 bolt torque is a hold point. Bolt torqueing must be witnessed by an EPCM representative prior to closing the Panel or terminal box. |  |  |  |
| --- | --- | --- | --- |
| Cable Termination At Source (Point of Supply) EPCM Witnessed by: N/A |  |  |  |
| Name: |  | Title: |  |
| Signature: |  | Date: |  |
| Cable Termination At Destination EPCM Witnessed by: N/A |  |  |  |
| Name: |  | Title: |  |
| Signature: |  | Date: |  |

| Item | Description |  |  |  | OK | N/A | Punch |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Completion |  |  |  |  |  |  |  |
|  |  | Confirm terminals are correctly tensioned. |  |  |  |  |  |
|  |  | Confirm Circuit left safe and ready for energisation. |  |  |  |  |  |
|  |  | Confirm Digital photos of significant cables/terminations are available ( ≥70 mm2). |  |  |  |  |  |
|  |  | Confirm As Built changes marked up on drawings/schedules. |  |  |  |  |  |
|  |  | Confirm terminal box covers are replaced. |  |  |  |  |  |
| DIGITAL PHOTOGRAPHS |  |  |  |  |  |  |  |
| Photo ID |  |  | Description | Taken By |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an authorised electrical worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |