| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |  |  |  |
| Manufacturer. |  |  | «ManufacturerName» |  | Model No. |  | «OEMPartlNumber» |  |  |  |
| Field to record Serial No. |  |  | «SerialNumber» |  |  |  |  |  |  |  |
| Drawing No. |  |  | «DocumentList» |  | Task No. |  | «TaskName» |  |  |  |
| Additional Information: |  |  | «Comments» |  |  |  |  |  |  |  |
| MOTOR DATA |  |  |  |  |  |  |  |  |  |  |
| Manufacturer |  |  |  | Motor Power (kW) |  |  |  |  |  |  |
| Type |  |  |  | Motor Serial No. |  |  |  |  |  |  |
| Frame |  |  |  | Mounting |  |  |  |  |  |  |
| FL RPM |  |  |  | Motor Insulation Class |  |  |  |  |  |  |
| Volts Stator |  |  |  | No. of Poles |  |  |  |  |  |  |
| Amps Stator |  |  |  | Volts Rotor |  |  |  |  |  |  |
| Rotation (Drive end) |  | CW / CCW |  | Amps Rotor |  |  |  |  |  |  |
| Anti-con Heaters |  |  |  | Heater Rating |  |  |  |  |  |  |
| Winding Thermistors |  |  |  | Motor RTD(s) |  |  |  |  |  |  |
| Motor Efficiency Class |  |  |  | HA Classification |  |  |  |  |  |  |
| Item | Description |  |  |  |  |  |  | OK | N/A | Punch |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and Schematic. Complete the table above. |  |  |  |  |  |  |  |  |  |
|  | Confirm Layout, location and orientation is correct against design drawings. |  |  |  |  |  |  |  |  |  |
|  | Confirm equipment is free from damage and debris. |  |  |  |  |  |  |  |  |  |
|  | Confirm phasing and phase labels on connections are as per AS1359, i.e. For clockwise rotation when viewed from drive end (facing shaft), connection is UVW = RWB. |  |  |  |  |  |  |  |  |  |
|  | Confirm auxiliary fan, slip ring and instrumentation terminal boxes are correctly labelled and secure to frame where applicable. |  |  |  |  |  |  |  |  |  |
|  | Confirm winding links are installed as per the datasheet – Delta or Star. |  |  |  |  |  |  |  |  |  |
|  | Confirm terminations to ensure that all nuts, washers and spring washers are in place. |  |  |  |  |  |  |  |  |  |
|  | Confirm that all terminations are tight and where torque settings are required, that correct values have been obtained and connection has been marked to indicate completion. |  |  |  |  |  |  |  |  |  |
|  | Confirm all gaskets and seals are intact. |  |  |  |  |  |  |  |  |  |
|  | Confirm glands are properly installed as per manufacturer’s recommendations and unused cable entries plugged. |  |  |  |  |  |  |  |  |  |
|  | Confirm gland plate is secure, earthed and gasket is in place. |  |  |  |  |  |  |  |  |  |
|  | Confirm all Earth bonding is as per design and specifications. |  |  |  |  |  |  |  |  |  |
|  | Confirm cooling tubes and veins clear and free of obstruction and confirm cleanliness. |  |  |  |  |  |  |  |  |  |
|  | If applicable, confirm that the wound rotor brush material is as per the manufacturer’s data sheet. |  |  |  |  |  |  |  |  |  |

| CONTINUITY, PHASING & EARTH CONTINUITY |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Winding Resistance | Resistance | Terminated Colour (RWB) |
| U1 – U2 |  | U = |
| V1 – V2 |  | V = |
| W1 – W2 |  | W = |
| Confirm motor connection is as per design | Star Delta |  |
| Earthing | Resistance | Remarks |
| 1 TB Frame-PE |  |  |
| 2 TB Frame-PE |  |  |
| 3 TB Frame-PE |  |  |
| Motor Frame-EP Bond Structure |  |  |
| Confirm Bonding To TB Lids |  |  |
| Thermistors (Indicate Colour Code) | Resistance | Remarks |
| RTDs N/A |  |  |
| (Indicate Colour Code) | Resistance Remarks | Remarks |
| Rø RTD |  |  |
| Wø RTD 1 |  |  |
| Bø RTD 1 |  |  |
| Rø RTD 2 |  |  |
| Wø RTD 2 |  |  |
| Bø RTD 2 |  |  |
| Motor inlet air |  |  |
| Motor DE bearing |  |  |
| Motor NDE bearing |  |  |
| Ambient Temperature: |  |  |

| LOW VOLTAGE MOTOR INSULATION RESISTANCE TEST (LOW VOLTAGE MOTOR) N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  | Calibration Due Date: |  |  |  |
| Test Point | U to V | V to W |  | W to U | UVW to E |  | Heater Circuit to E |  |  |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC | 500 VDC |  | 500 VDC |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ | MΩ |  | MΩ |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass | Fail |

| HIGH VOLTAGE MOTOR INSULATION RESISTANCE TEST N/A |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  | Calibration Due Date: |  |  |
| Test Point | U to V | V to W |  | W to U | Heater Circuit to E |  |  |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC | 500 VDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ | MΩ |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| MOTOR POLARISATION INDEX AND INSULATION TEST (HIGH VOLTAGE MOTOR ONLY) N/A |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  |  | Calibration Due Date: |  |  |
| Test Point | UVW to E |  |  |  |  |  |  |
| Test Voltage | 5 kVDC |  |  |  |  |  |  |
| Test Duration | @1 Minute |  |  | @10 Minutes |  |  |  |
| Result (MΩ) | MΩ |  |  |  |  |  |  |
| PI Ratio (PI) |  |  |  |  |  |  |  |
| Ambient Temp. |  |  |  |  |  |  |  |
| Winding Temp. |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |

| CONTACT RESISTANCE (DUCTOR) TEST N/A |  |  |  |  | BOLT TORQUE N/A |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Note: Motor winding terminal contact resistance (If practical) and winding bolt torque verification records are only required on Motors 75 kW and above. Test is only applicable to winding terminals prior to final supply cable termination. |  |  |  |  |  |  |  |  |  |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |
| Torque Wrench Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |
| Test Point | Micro Ohms | Test Point |  | Micro Ohms | Termination | Torque Nm |  | Termination | Torque Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |
|  | µΩ |  |  | µΩ |  | Nm |  |  | Nm |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all motor windings are discharged to Earth after testing. |  |  |  |
|  | Confirm equipment integrity - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm all enclosures are left clean and free from debris. |  |  |  |
|  | Confirm all terminal box covers are replaced and gaskets are undamaged. |  |  |  |
|  | Confirm equipment is left safe ready for energisation. |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Digital photos required: All name plates inclusive or Motor/Stator, Rotor, Heaters and Thermistors and RTDs. For Motors 75 kW and above general installation photos with terminal covers off. |  |  |  |
| Photo ID |  | Description | Taken By |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |