| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Nameplate Details as per Datasheet and Equipment Labeling is as per GA and Schematic. |  |  |  |
|  | Confirm data sheet and Factory Acceptance Test results are available. |  |  |  |
|  | Confirm equipment is level, details of foundation / plinth and clearance distances are as per design. |  |  |  |
|  | Confirm Layout, location and orientation is correct against design drawings. |  |  |  |
|  | Confirm mechanical operation is unimpeded, IP rating is not compromised, NER is free from damage, rust, contamination and debris internally and externally. |  |  |  |
|  | Confirm gland plate is secure, earthed and gasket is in place. |  |  |  |
|  | Confirm Glands are properly installed as per manufacturer’s recommendations and unused cable entries plugged. |  |  |  |
|  | Confirm control wiring is as per schematic drawings. |  |  |  |
|  | Confirm all wires are ferruled and ferrules are correct. |  |  |  |
|  | Confirm Terminals are secure and terminal numbering is in place and correct, terminations are tight with one core per terminal. |  |  |  |
|  | Confirm terminations to ensure that all nuts, washers and spring washers are in place |  |  |  |
|  | Confirm that all terminations are tight and where torque settings are required, that correct values have been obtained and connection has been marked to indicate completion. |  |  |  |
|  | Confirm NER CTs are installed, terminated and securely mounted as per design. |  |  |  |
|  | Confirm resistor bank stand-off insulators are clean and resistors are mounted correctly and securely. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| CONTINUITY & EARTH TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Resistance | Remarks |
| E-EBar |  |  |
| E- Gland Plate |  |  |
| E-Door(s) |  |  |
| Point to Point Confirmed Y N | Continuity OK Pass Fail |  |

| NER RESISTORS - RESISTANCE TEST / CHECK |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  |  | Calibration Due Date: |  |  |  |  |  |  |
| Note: Test NER resistance value end to end if within 10% of data sheet design value then individual resistor actual values not required. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NER Total | Resistor 1 | Resistor 2 |  | Resistor 3 | Resistor 4 | Resistor 5 |  | Resistor 6 | Resistor 7 | Resistor 8 |  | Resistor 9 |  |
| Design Ω |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Actual Ω | Ω | Ω |  | Ω | Ω | Ω |  | Ω | Ω | Ω |  | Ω |  |
| Resistance Value |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |

| NER INSULATION - RESISTANCE TEST (5 kV Test Voltage) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No. |  | Calibration Due Date: |  |  |
| Test Point | N to E |  |  |  |  |  |
| Test Voltage | 5 kVDC |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all sections are discharged to Earth. |  |  |  |
|  | Confirm enclosure integrity and bus separation - Neutral to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt – Neutral to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm NER is left clean, free from debris and test tools. |  |  |  |
|  | Replace all covers and confirm the Cubicle is safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |