| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  |  |  |  | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |  |  |  |
| Drawing No. |  | «DocumentList» |  |  |  |  | Task No. | «TaskName» |  |
| Additional Information: |  | «Comments» |  |  |  |  |  |  |  |
| EQUIPMENT NAME PLATE |  |  |  |  |  |  |  |  |
| Location: |  |  | Pole: |  | Transformer ID: |  |  |  |
| TRANSFORMER DETAILS |  |  |  |  |  |  |  |  |
| Manufacturer: | Year Manufacture: |  |  | Vector Group: |  | Serial Number: |  |  |
| Impedance - %: | Insul. Liquid Type: |  |  | Insul. Liquid Vol. - litres: |  | Cooling Type: |  |  |
| Primary Voltage – V: | Secondary Voltage – V: |  |  | Rating – kVA: |  | Total Mass - kg: _____ Un-tanking Mass – kg: _____ |  |  |
| INSTALLATION DESIGN |  |  |  |  |  |  |  |  |
| Tap Position Setting: | Surge Arrestor Voltage: Type: MWK |  |  | HV Fuse: |  | LV Fuse: |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. Complete the table above. |  |  |  |
|  | Confirm transformer location and orientation is correct, it has been mounted on the pole/ cross-arm as per design and all mounting hardware and fasteners are secure and torqued. |  |  |  |
|  | Confirm all components are free from damage, contamination or corrosion. |  |  |  |
|  | Confirm that all manufacturers Type, Routine and Special Test documentation is available as requested by the applicable Equipment Data Sheet and supply scope. |  |  |  |
|  | Confirm phase indication/ marking has been fitted where required. |  |  |  |
|  | Confirm Line and load links installed and connected correctly. |  |  |  |
|  | Confirm conductor clearances to pole, earth and other conductors. |  |  |  |
|  | Confirm and operate the tap changer then set tap changer to nominal tap position. |  |  |  |
|  | Confirm tank oil level. |  |  |  |
|  | Inspect tank condition and check for oil leaks and spills. |  |  |  |
|  | Inspect the condition of the radiator fins. |  |  |  |
|  | Confirm bushings are clean, in good condition (No oil leaks). |  |  |  |
|  | Confirm surge arrestors are of correct specified voltage, if applicable. |  |  |  |
|  | Confirm cable installation and determine zero stress on bushings. |  |  |  |
|  | Confirm auxiliary hardware has been installed correctly as per design. |  |  |  |
|  | Confirm that auxiliary HV and LV fuses have been installed correctly as per design and are of the specified rating. |  |  |  |
|  | Confirm that surge arrestor earths are connected correctly and tight. |  |  |  |
|  | Confirm all earthing is as per design and is securely fitted. |  |  |  |
|  | Confirm all operational items are correctly labelled as per schematic diagram. |  |  |  |
|  | Confirm neutral connected and earthed and MEN/N-link connected. |  |  |  |
|  | Attach digital photos illustrating pole top transformer installation. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| INSTALLATION CONTINUITY, PHASING & EARTH |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| TX to OHL Connections | Phase Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| A-A (Primary) |  | Ω |
| B-B (Primary) |  | Ω |
| C-C (Primary) |  | Ω |
| a-a (Secondary) |  | Ω |
| b-b (Secondary) |  | Ω |
| c-c (Secondary) |  | Ω |
| n-n (Secondary) |  | Ω |
| Main E-E Bar |  | Ω |
| TX Tank E-E Bar |  | Ω |
| Phase Check/Markings Confirmed Y N | Continuity OK Pass Fail |  |

| WINDING RESISTANCE (CONTINUITY) TEST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: |  | Calibration Date: |
| Primary Winding |  |  | Secondary Winding |  |
| Test Points | Resistance |  | Test Points | Resistance |
| A-B |  |  | a-n |  |
| B-C |  |  | b-n |  |
| C-A |  |  | c-n |  |
| Resistance Confirmed Y N |  |  |  |  |

| WINDING RATIO TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No.: |  |  |  |  |  | Calibration Date: |  |  |
| Tap | Calc Ratio | A Phase |  |  |  | B Phase |  |  | C Phase |  |  |  |
|  |  | Ratio | I (mA) |  | Ph (deg) | Ratio | I (mA) | Ph (deg) | Ratio |  | I (mA) | Ph (deg) |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |
| Winding Ratio Test Confirmed Y N |  |  |  |  |  |  |  |  |  |  |  |  |

| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |  |
| Test Point | (Pri) to (Earth) (Secondary Earthed) |  | (Sec) to (Earth) (Primary Earthed) |  | (Pri) to (Sec) |  |  |
| Test Voltage | 5 kVDC |  | 1 kVDC |  | 5 kVDC |  |  |
| Test Duration |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  | MΩ |  | MΩ |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Digital photos required: Digital photos of significant terminations and general installation are to be identified and submitted with this ITR. |  |  |  |
| Photo ID |  | Description | Taken By |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm conductor clearances to pole, phase to phase and phase to earth clearance distances have been maintained and have been unaltered as per design. |  |  |  |
|  | Confirm the Pole top Transformer is safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |