| Tag No. «Name» - «Description» |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  | OEM Part No. | «OEMPartNumber» |  |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |
| Drawing No. |  | «DocumentList» |  | Task No. | «TaskName» |  |
| Additional Information: |  | «Comments» |  |  |  |  |
| TRANSFORMER DETAIL |  |  |  |  |  |  |
| Manufacturer |  |  | Type of Tank |  |  |  |
| Serial No. |  |  | Oil Level Indicator |  |  |  |
| Rating |  |  | Oil Temp Indicator |  |  |  |
| Vector Group |  |  | Winding Temp Relay |  |  |  |
| Primary Voltage |  |  | Bucholz Relay |  |  |  |
| Secondary Voltage |  |  | Pressure Relief Vent |  |  |  |
| Primary Current |  |  | Rapid Press Rise Relay |  |  |  |
| Secondary Current |  |  | Tap Changer Type |  |  |  |
| Impedance Voltage |  |  | Oil Drain Valve |  |  |  |
| Insulation Level |  |  | Top Oil Valve |  |  |  |
| Insulation Liquid Volume |  |  | Radiator Type |  |  |  |
| Total Mass |  |  | Cooling Fans |  |  |  |
| Year of Manufacture |  |  | Oil Pumping |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| TEST NOTES: |  |  |  |  |
| PRE-REQUISITES |  |  |  |  |
|  | Confirm Equipment Data Sheet is available. |  |  |  |
|  | Confirm that all manufacturers Type, Routine and Special Test documentation is available as requested by the applicable Equipment Data Sheet and supply scope. |  |  |  |
|  | If applicable, confirm FAT calibration records for Top Oil and WTI instrumentation (attach record to this ITR). |  |  |  |
|  | If applicable, confirm FAT HV power frequency withstand RMS Test results are available (attach record to this ITR). If results are not available or site reassembly has occurred carry out the HV testing within this ITR in accordance with the manufacturers Test procedure. |  |  |  |
|  | If applicable, confirm FAT HV auxiliary and control circuit power frequency withstand Test results are available (attach record to this ITR). If results are not available or site reassembly has occurred, carry out the HV testing within this ITR in accordance with the manufacturers Test procedure. |  |  |  |
|  | If applicable (Data Sheet), confirm FAT Winding DF and CAP Test results are available (attach record to this ITR). |  |  |  |
|  | If applicable (Data Sheet), confirm FAT Bushing DF and CAP Test results are available (attach record to this ITR). |  |  |  |
|  | If applicable (Data Sheet), confirm FAT Load Losses (Leakage Reactance) Test results are available (attach record to this ITR). |  |  |  |
|  | If applicable (Data Sheet), confirm FAT Dielectric Response (DFRA) Test results are available (attach record to this ITR). |  |  |  |
|  | If applicable (Data Sheet), confirm FAT Sweep Frequency Response Analysis (SFRA) (attach record to this ITR). |  |  |  |
|  | If applicable (Data Sheet), confirm FAT No Load Loss Test results are available (attach record to this ITR). |  |  |  |
|  | Confirm equipment and circuit is safely isolated/ disconnected on primary and secondary sides. |  |  |  |
| PHYSICAL CHECKS |  |  |  |  |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. Complete the table above. |  |  |  |
|  | Confirm Layout, location and orientation is correct against design drawings |  |  |  |
|  | Confirm equipment is level, details of foundation/ plinth and clearance distances are as per design. |  |  |  |
|  | Confirm equipment is free from damage and debris |  |  |  |
|  | Confirm cable size and type is correct as per the cable schedule. |  |  |  |
|  | Confirm all field tests completed as per manufacturers pre-energisation procedure. |  |  |  |
|  | Confirm Tap Changer manual operation. |  |  |  |
|  | Confirm tap changer set to nominal tap position. |  |  |  |
|  | Confirm the condition of the radiators. |  |  |  |
|  | Confirm the condition of the fans. |  |  |  |
|  | Confirm for oil leaks and spills. |  |  |  |
|  | Confirm all earthing connection points are tight. |  |  |  |
|  | Confirm oil levels in conservator tank. |  |  |  |
|  | Bleed and confirm oil level in tap changer compartment. |  |  |  |
|  | Confirm pin of pressure relief valve is not pushed out. |  |  |  |
|  | Confirm explosion vent diaphragm is not broken. |  |  |  |
|  | Confirm silica gel breather crystals are blue and breather cup is filled with oil. |  |  |  |
|  | Confirm all external HV and LV terminations are tight. |  |  |  |
|  | Confirm winding temperature indicator reading, taking account of ambient temp. |  |  |  |
|  | Confirm oil temperature indicator, taking account of ambient temp. |  |  |  |
|  | Reset maximum indicator pointers on Winding Temperature Indicator (WTI) and Operational Time Interval (OTI). |  |  |  |
|  | Record oil temperature manual alarm setting ______ |  |  |  |
|  | Record oil temperature manual trip setting ______ |  |  |  |
|  | Record fan cut in manual temperature setting _______ |  |  |  |
|  | Record winding temperature manual alarm setting ________ |  |  |  |
|  | Record winding temperature manual trip setting ________ |  |  |  |
|  | Confirm the winding temperature gauge. |  |  |  |
|  | Confirm oil level in Buchholz relay. |  |  |  |
|  | Inspect the condition of the Buchholz relay. |  |  |  |
|  | Confirm if gas is detected in the conservator. |  |  |  |
|  | Confirm all cable box bolts and nuts are tight |  |  |  |
|  | Confirm all bleed plugs are tight. |  |  |  |
|  | Confirm paintwork is satisfactory. |  |  |  |
|  | Inspect condition of all Instruments. |  |  |  |
|  | Confirm radiator oil valves are open. |  |  |  |
|  | Confirm Oil Sample has been taken or results are available. |  |  |  |
|  | Confirm site clean-up at completion of tasks. |  |  |  |

| CONTINUITY, PHASING & EARTH |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Resistance | Remarks |
| R-W-B Phase Marking |  |  |
| TX Tank E - E Bar 1 & 2 | / |  |
| TX Sec N – E |  |  |
| TX Aux Equip – E Bonding | / / / / / / / / / |  |
| Point to Point Confirmed Y N | Continuity Compliance Pass Fail |  |

| WINDING RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  | Calibration Date: |  |  |
| Primary Winding |  |  |  |  | Secondary Winding 1 |  |  |  |
| Tap Position | A Resistance | B Resistance |  | C Resistance | Tap Position | Resistance |  |  |
| 1 | Ω | Ω |  | Ω | a1-n | Ω |  |  |
| 2 | Ω | Ω |  | Ω | b1-n | Ω |  |  |
| 3 | Ω | Ω |  | Ω | c1-n | Ω |  |  |
| 4 | Ω | Ω |  | Ω |  |  |  |  |
| 5 | Ω | Ω |  | Ω |  |  |  |  |
| 6 | Ω | Ω |  | Ω |  |  |  |  |
| 7 | Ω | Ω |  | Ω |  |  |  |  |
| 8 | Ω | Ω |  | Ω |  |  |  |  |
| 9 | Ω | Ω |  | Ω |  |  |  |  |
| 10 | Ω | Ω |  | Ω |  |  |  |  |
| 11 | Ω | Ω |  | Ω |  |  |  |  |
| 12 | Ω | Ω |  | Ω |  |  |  |  |
| 13 | Ω | Ω |  | Ω |  |  |  |  |
| 14 | Ω | Ω |  | Ω |  |  |  |  |
| 15 | Ω | Ω |  | Ω |  |  |  |  |
| 16 | Ω | Ω |  | Ω |  |  |  |  |
| 17 | Ω | Ω |  | Ω |  |  |  |  |
| 18 | Ω | Ω |  | Ω |  |  |  |  |
| 19 | Ω | Ω |  | Ω |  |  |  |  |
| 20 | Ω | Ω |  | Ω |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| TURN RATIO TEST |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  |  | Serial No.: |  |  |  | Calibration Date: |  |  |  |  |
| Tap Position | Calc Ratio | A Phase |  |  |  | B Phase |  |  | C Phase |  |  |  |  |
|  |  | Ratio | I (mA) | Ph (deg) |  | Ratio | I (mA) | Ph (deg) | Ratio | I (mA) |  | Ph (deg) |  |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name Plate Ratio:______ Winding Turn Ratio |  |  |  |  |  |  |  |  |  |  | Pass |  | Fail |

| AUXILLIARY & CONTROL CIRCUIT INSULATION RESISTANCE TEST ) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  |  | Serial No. |  |  | Calibration Date: |  |  |  |  |
| Test Point | R to W | R to B | W to B | R to N | W to N | B to N | RWB to E |  | N to E |  |
| Test Voltage | 1 kVDC | 1 kVDC | 1 kVDC | 1 kVDC | 1 kVDC | 1 kVDC | 1 kVDC |  | 1 kVDC |  |
| Test Duration | 1 minute | 1 minute | 1 minute | 1 minute | 1 minute | 1 minute | 1 minute |  | 1 minute |  |
| Aux Equip /Test Configuration |  |  |  |  |  |  |  |  |  |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| / | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ | MΩ |  | MΩ |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass |  | Fail |

| WINDING INSULATION RESISTANCE AND POLARISATION INDEX TEST |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |  |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |  |
| Test Point | (A+B+C) to (a1+b1+c1)+E |  | (a1+b1+c1) to (A+B+C)+E |  | Tertiary (X+Y+Z) to (A+B+C+a1+b1+c1)+E |  |  |
| Test Voltage | 5 kVDC |  | 1 kVDC |  | 5 kVDC |  |  |
| IR @ 1 Minute | MΩ |  | MΩ |  | MΩ |  |  |
| PI @ 1 Minute |  |  |  |  |  |  |  |
| IR @ 10 Minutes | MΩ |  | MΩ |  | MΩ |  |  |
| PI @ 10 Minutes |  |  |  |  |  |  |  |
| Ambient Temperature ____ Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all bus sections are discharged to Earth. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Replace all covers and confirm the transformer is safe and ready for energisation. |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Digital photos required: Digital photos of significant terminations and name plates are to be identified and submitted with this ITR. |  |  |  |
| Photo ID |  | Description | Taken By |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |