| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| Note: This ITR is intended for overhead line (OHL) distribution systems 33 kV and below as per SS-E109. For distribution and transmission systems above 33 kV then direction will be provided by the engineer. |  |  |  |  |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA. |  |  |  |
|  | Confirm correct signage has been installed as per design. |  |  |  |
|  | Confirm location and orientation is correct |  |  |  |
|  | Confirm the overall pole installation is with the installation specification tolerances |  |  |  |
|  | Confirm all components are free from damage, contamination or corrosion. |  |  |  |
|  | Confirm phase indication/ marking has been fitted where required. |  |  |  |
|  | Confirm the cross arm and all equipment is correctly installed and securely mounted. |  |  |  |
|  | Confirm insulators are as per design, are the correct type and rating, are clean, undamaged, complete and installed correctly. |  |  |  |
|  | Confirm that the pole embedded depth is as per the drawing. |  |  |  |
|  | Confirm that no subsidence of backfill has occurred around the pole. |  |  |  |
|  | Confirm stays and stay insulators for correct installation and tension. |  |  |  |
|  | Confirm that there is no subsidence around the stay block. |  |  |  |
|  | Confirm that all stay/ guy wires are effectively bonded to the pole earthing system or insulator installed. |  |  |  |
|  | Confirm conductor installation and determine minimal stress on insulator stand-offs. |  |  |  |
|  | Confirm that surge arrestor earths are connected correctly and tight. |  |  |  |
|  | Confirm bird strike protection has been installed as per design. |  |  |  |
|  | Confirm all earthing is as per design, is securely fitted and continuity results recorded in table |  |  |  |
|  | Confirm conductor separation and clearances to pole, earth, other conductors and auxiliary pole hardware. |  |  |  |
|  | All operational items are correctly labelled as per the specification or standard drawings. |  |  |  |
|  | If Applicable attach digital photos are recorded as required. (Digital photos only required for poles with additional hardware or non-standard configurations) |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| EARTH CONTINUITY (All EP Bonds, Grids, Matts & Stakes N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Instrument Used: |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  |  |  | Serial No.: |  |  |  |  | Calibration Date: |  |
| Test Point A ID |  | Test Point B ID |  |  | Resistance (Ω) |  | Test Point A ID | Test Point B ID |  |  |  | Resistance (Ω) |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
|  |  |  |  |  | Ω |  |  |  |  |  |  | Ω |
| Point to Point Confirmed Y N |  |  |  |  |  |  | Continuity Compliance Pass Fail |  |  |  |  |  |
| EARTH LOOP IMPEDANCE (CLAMP ON TEST) N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| Instrument Used: |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  |  |  | Serial No.: |  |  |  |  | Calibration Date: |  |
| Attach layout drawing to indicate test points |  |  |  |  |  |  |  |  |  |  |  |  |
| Test No. |  | Test Point |  |  |  |  |  |  |  | Resistance (Ω) |  |  |
| Earth Stake #1 |  |  |  |  |  |  |  |  |  |  |  |  |
| Earth Stake #2 |  |  |  |  |  |  |  |  |  |  |  |  |
| Results Acceptable Pass Fail |  |  |  |  |  |  |  |  |  |  |  |  |
| DIGITAL PHOTOGRAPHS |  |  |  |  |  |  |  |  |  |  |  |  |
| Digital photos required: Digital photos of significant terminations are to be identified and submitted with this ITR. Not applicable for standard or intermediate poles. |  |  |  |  |  |  |  |  |  |  |  |  |
| Photo ID |  |  |  | Description |  |  |  |  | Taken By |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |