| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cable Type: | «CableType» | Cable Rating: |  | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: | «CableSize» |  |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| Note: This ITR is intended for overhead line (OHL) distribution systems 33 kV and below as per SS-E109. For distribution and transmission systems above 33 kV then direction will be provided by the engineer. |  |  |  |  |
|  | Confirm the conductor size and specification is correct. |  |  |  |
|  | Confirm all equipment is free from mechanical damage. |  |  |  |
|  | Confirm conductor height markers are installed at crossings and clearance distances are maintained as per specification. |  |  |  |
|  | Confirm signs and height indicators are installed at all road crossings as per specification. |  |  |  |
|  | Confirm conductor span, set out and earth wire are installed as per design. |  |  |  |
|  | Confirm Pole jewellery is installed as per design leading into and out of pole terminations |  |  |  |
|  | Confirm sag calculations/profiles and actual sag measurement is as per design and drawings. (Attach sag measurements) |  |  |  |
|  | Confirm conductor tension is within design calculations (Attach conductor tension results) |  |  |  |
|  | Confirm conductor & jumper clearance distances between phases & phase to earth are as per design & drawings. |  |  |  |
|  | Confirm dampers are installed correctly and correctly spaced |  |  |  |
|  | Confirm all compression joints are installed correctly and as per design |  |  |  |
|  | Confirm phasing on overall length of line. |  |  |  |
|  | Confirm phase markers are fitted. |  |  |  |
|  | Confirm that Optical Power Ground Wire (OPGW) canisters are in correct locations. |  |  |  |
|  | Confirm vibration dampening is installed as per design. |  |  |  |
|  | Confirm OPGW fibre break out is in accordance with manufacturers specifications. |  |  |  |
|  | Confirm there is sufficient excess fibre length to ensure stress free installation service. |  |  |  |
|  | Confirm there is no undue stress on terminations. |  |  |  |
|  | Confirm insulator connection bolts are tight. |  |  |  |
|  | Confirm the conductors are tied correctly to insulators. |  |  |  |
|  | Confirm the conductor splices and grips are satisfactory. |  |  |  |
|  | Confirm all as-built drawings are completed. |  |  |  |
|  | Carry out 100% check of Contact Resistance for Joints and terminations and 100% Torque checks (Complete results below or attach results or additionally assign E1.004 & E1.005) |  |  |  |
|  | Note any defects for remedial action on punchlist form. |  |  |  |

| PHASING & CONTINUITY TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Connections | Phase Check (Initial Pass/Fail) | Continuity Confirm – Result Ω |
| R-R |  | Ω |
| B-B |  | Ω |
| W-W |  | Ω |
| E-E |  | Ω |
| Phase Point to Point Confirmed Y N | Continuity Compliance Pass Fail | Resistor setting: Ω |

| HIGH VOLTAGE INSULATION (IR) TEST |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. | Calibration Date |  |  |  |
| Test Voltage: 5kV |  |  |  |  |  |  |  |
| Phase | IR Test Configuration |  |  |  |  |  |
| PHASE A | (B+C) Earthed Far End + (B+C) Earthed at Near End |  |  |  |  |  |
|  | Result: GΩ | (PASS ≥ 10 GΩ) |  |  |  |  |
| PHASE B | (A+C) Earthed Far End + (A+C) Earthed at Near End |  |  |  |  |  |
|  | Result: GΩ | (PASS ≥ 10 GΩ) |  |  |  |  |
| PHASE C | (A+B) Earthed Far End + (A+B) Earthed at Near End |  |  |  |  |  |
|  | Result: GΩ | (PASS ≥ 10 GΩ) |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  | Pass | Fail |  |

| CONDUCTOR JOINT CONTACT RESISTANCE - DUCTOR TEST Supporting evidence attached |  |  |  |  | BOLT TORQUE (100% Check) Supporting evidence attached |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |  |  |
| Test Point | Resistance | Test Point |  | Resistance | Test Point | Torque Nm |  | Test Point |  | Torque Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
|  | µΩ |  |  | µΩ |  | Nm |  |  |  | Nm |  |
| Contact Resistance Test Current: ____ Contact Resistance Test Compliance |  |  |  |  |  |  |  |  | Pass |  | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all cables are discharged to Earth. |  |  |  |
|  | Confirm conductor clearances to pole, phase to phase and phase to earth clearance distances have been maintained and have been unaltered as per design. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |